| ## Form A2-1: Compliance Verification Report for Synchronous and Asynchronous (non inverter) Power Generating Modules up to and including 50 kW This form should be used by the Manufacturer to demonstrate and declare compliance with the requirements of EREC G99. The form can be used in a variety of ways as detailed below: - To obtain Fully Type Tested status The Manufacturer can use this form to obtain Fully Type Tested status for a Power Generating Module by registering this completed form with the Energy Networks Association (ENA) Type Test Register. Tests 1 – 14 must all be completed and compliant for the Power Generating Module to be classified as Fully Type Tested. - To obtain Type Tested status for a product This form can be used by the Manufacturer to obtain Type Tested status for a product which is used in a Power Generating Module by registering this form with the relevant parts completed with the Energy Networks Association (ENA) Type Test Register. Where the Manufacturer is seeking to obtain Type Tested status for an Interface Protection device the appropriate section of Form A2-4 should be used. - One-off Installation This form can be used by the Manufacturer or Installer to confirm that the Power Generating Module has been tested to satisfy all or part of the requirements of this EREC G99. This form shall be submitted to the DNO as part of the application. A combination of (2) and (3) can be used as required, together with Form A2-4 where compliance of the Interface Protection is to be demonstrated on site. Note: If the Power Generating Module is Fully Type Tested and registered with the Energy Networks Association (ENA) Type Test Register, the Installation Document (Form A3-1 or A3-2) should include the Manufacturer’s reference number (the system reference), and this form does not need to be submitted. Where the Power Generating Module is not registered with the ENA Type Test Register or is not Fully Type Tested this form (all or in parts as applicable) needs to be completed and provided to the DNO, to confirm that the Power Generating Module has been tested to satisfy all or part of the requirements of this EREC G99. Where the Registered Capacity is lower than the Intrinsic Design Capacity, all results of tests must be based on the Registered Capacity, and not on the Intrinsic Design Capacity. |  |  |  |  |
| --- | --- | --- | --- | --- |
| PGM technology |  |  |  |  |
| Manufacturer name |  |  |  |  |
| Address |  |  |  |  |
| Tel. |  |  | Web site |  |
| E:mail |  |  |  |  |
| Registered Capacity |  | kW |  |  |

| There are four options for Testing: (1) Fully Type Tested, (2) Type Tested product, (3) one-off installation, (4) tested on site at time of commissioning. The check box below indicates which tests in this Form have been completed for each of the options. With the exception of Fully Type Tested PGMs tests may be carried out at the time of commissioning (Form A2-4). Include reference(s) for Manufacturers’ Information including the ENA Type Test Register system reference number where applicable. |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Tested option: |  | 1. Fully Type Tested |  | 2. Type Tested product |  | 3. One-Off Manufactures’ Info. | 4. Tested on Site at time of Commissioning |
| 0. Fully Type Tested- all tests detailed below completed and evidence attached to this submission |  |  |  | N/A |  | N/A | N/A |
| 1. Operating Range |  | N/A |  |  |  |  |  |
| 2. PQ – Harmonics |  |  |  |  |  |  |  |
| 3. PQ – Voltage Fluctuation and Flicker |  |  |  |  |  |  |  |
| 4. Power Factor (PF) |  |  |  |  |  |  |  |
| 5. Frequency protection trip and ride through tests |  |  |  |  |  |  |  |
| 6. Voltage protection trip and ride through tests |  |  |  |  |  |  |  |
| 7. Protection – Loss of Mains Test, Vector Shift and RoCoF Stability Test |  |  |  |  |  |  |  |
| 8. LFSM-O Test |  |  |  |  |  |  |  |
| 9. Power Output with Falling Frequency Test |  |  |  |  |  |  |  |
| 10. Protection – Reconnection Timer |  |  |  |  |  |  |  |
| 11. Fault Level Contribution |  |  |  |  |  |  |  |
| There are four options for Testing: (1) Fully Type Tested, (2) Type Tested product, (3) one-off installation, (4) tested on site at time of commissioning. The check box below indicates which tests in this Form have been completed for each of the options. With the exception of Fully Type Tested PGMs tests may be carried out at the time of commissioning (Form A2-4). Include reference(s) for Manufacturers’ Information including the ENA Type Test Register system reference number where applicable. |  |  |  |  |  |  |  |
| Tested option: |  | 1. Fully Type Tested |  | 2. Type Tested product |  | 3. One-Off Manufactures’ Info. | 4. Tested on Site at time of Commissioning |
| 12. Wiring functional tests if required by para 15.2.1 (attach relevant schedule of tests) |  |  |  |  |  |  |  |
| 13. Logic Interface (input port) |  |  |  |  |  |  |  |
| 14. Cyber security |  |  |  |  |  |  |  |
| Manufacturer compliance declaration - I certify that all products supplied by the company with the above Type Tested Manufacturer’s reference number will be manufactured and tested to ensure that they perform as stated in this document, prior to shipment to site and that no site Modifications are required to ensure that the product meets all the requirements of EREC G99. |  |  |  |  |  |  |  |
| Signed |  |  | On behalf of |  |  |  |  |
| Note that testing can be done by the Manufacturer of an individual component (ie product) or by an external test house. Where parts of the testing are carried out by persons or organisations other than the Manufacturer then that person or organisation shall keep copies of all test records and results supplied to them to verify that the testing has been carried out by people with sufficient technical competency to carry out the tests. |  |  |  |  |  |  |  |

| A2-1 Compliance Verification Report –Tests for Type A Synchronous Power Generating Modules up to and including 50 kW – test record |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1. Operating Range: Tests should be carried with the Power Generating Module operating at Registered Capacity and connected to a suitable test supply, grid simulation set or load bank. The power supplied by the primary source shall be kept stable within ± 5 % of the apparent power value set for the entire duration of each test sequence. Frequency, voltage and Active Power measurements at the output terminals of the Power Generating Module shall be recorded every second. The tests will verify that the Power Generating Module can operate within the required ranges for the specified period of time. The Interface Protection shall be disabled during the tests. Pass or failure of the test should be indicated in the fields below (right hand side), for example with the statement “Pass”, “No disconnection occurs”, etc. Graphical evidence is preferred. |  |  |  |  |  |  |  |  |  |  |
| Test 1 Voltage = 85% of nominal (195.5 V), Frequency = 47 Hz, Power Factor = 1, Period of test 20 s |  |  |  |  | Test results or chart to confirm operation |  |  |  |  |  |
| Test 2 Voltage = 85% of nominal (195.5 V), Frequency = 47.5 Hz, Power Factor = 1, Period of test 90 minutes |  |  |  |  | Test results or chart to confirm operation |  |  |  |  |  |
| Test 3 Voltage = 110% of nominal (253 V), Frequency = 51.5 Hz, Power Factor = 1, Period of test 90 minutes |  |  |  |  | Test results or chart to confirm operation |  |  |  |  |  |
| Test 4 Voltage = 110% of nominal (253 V), Frequency = 52.0 Hz, Power Factor = 1, Period of test 15 minutes |  |  |  |  | Test results or chart to confirm operation |  |  |  |  |  |
| Test 5 Voltage = 100% of nominal (230 V), Frequency = 50.0 Hz, Power Factor = 1, Period of test = 90 minutes |  |  |  |  | Test results or chart to confirm operation |  |  |  |  |  |
| Test 6 RoCoF withstand Confirm that the Power Generating Module is capable of staying connected to the Distribution Network and operate at rates of change of frequency up to 1 Hzs-1 as measured over a period of 500 ms. Note that this is not expected to be demonstrated on site. |  |  |  |  | Test results or chart to confirm operation |  |  |  |  |  |
| 2. Power Quality – Harmonics: The test requirements are specified in A.7.2.5. These tests should be carried out as specified in BS EN 61000-3-12, and measurements for the 2nd – 13th harmonics should be provided. The results need to comply with the limits of Table 2 of BS EN 61000-3-12 for single phase equipment and Table 3 of BS EN 610000-3-12 for three phase equipment. For three phase Power Generating Modules, measurements for all phases should be provided. The rating of the Power Generating Module (per phase) should be provided below and the Total Harmonic Distortion (THD) and Partial Weighted Harmonic Distortion (PWHD) should be provided at the bottom of this section. |  |  |  |  |  |  |  |  |  |
| Power Generating Module tested to BS EN 61000-3-12 |  |  |  |  |  |  |  |  |  |
| Power Generating Module rating per phase (rpp) |  |  |  |  |  | kVA |  | Harmonic % = Measured Value (A) x 23/rating per phase (kVA) |  |
| Single or three phase measurements (for single phase measurements, only complete L1 columns below) |  |  |  |  |  |  |  |  |  |
| Harmonic | At 45-55% of Registered Capacity21 |  |  |  |  |  |  | Limit in BS EN 61000-3-12 |  |
|  | Measured value (MV) in Amps |  |  | Measured value (MV) in % |  |  |  |  |  |
|  | L1 | L2 | L3 | L1 |  | L2 | L3 | 1 phase | 3 phase |
| 2 |  |  |  |  |  |  |  | 8% | 8% |
| 3 |  |  |  |  |  |  |  | 21.6% | Not stated |
| 4 |  |  |  |  |  |  |  | 4% | 4% |
| 5 |  |  |  |  |  |  |  | 10.7% | 10.7% |
| 6 |  |  |  |  |  |  |  | 2.67% | 2.67% |
| 7 |  |  |  |  |  |  |  | 7.2% | 7.2% |
| 8 |  |  |  |  |  |  |  | 2% | 2% |
| 9 |  |  |  |  |  |  |  | 3.8% | Not stated |
| 10 |  |  |  |  |  |  |  | 1.6% | 1.6% |
| 11 |  |  |  |  |  |  |  | 3.1% | 3.1% |
| 12 |  |  |  |  |  |  |  | 1.33% | .33% |
| 13 |  |  |  |  |  |  |  | 2% | 2% |

—————————

- See the note in A.7.2.5.1 if 45-55% of Registered Capacity is below the Minimum Stable Operating Level. If an alternative loading level is chosen, the level should be indicated on the test form and the reason for not testing at 45-55% of Registered Capacity should be stated in the box at the end of this section.

| THD22 |  |  |  |  |  |  | 23% | 13% |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| PWHD23 |  |  |  |  |  |  | 23% | 22% |
| Harmonic | At 100% of Registered Capacity |  |  |  |  |  | Limit in BS EN 61000-3-12 |  |
|  | Measured value (MV) in Amps |  |  | Measured value (MV) in % |  |  |  |  |
|  | L1 | L2 | L3 | L1 | L2 | L3 | 1 phase | 3 phase |
| 2 |  |  |  |  |  |  | 8% | 8% |
| 3 |  |  |  |  |  |  | 21.6% | Not stated |
| 4 |  |  |  |  |  |  | 4% | 4% |
| 5 |  |  |  |  |  |  | 10.7% | 10.7% |
| 6 |  |  |  |  |  |  | 2.67% | 2.67% |
| 7 |  |  |  |  |  |  | 7.2% | 7.2% |
| 8 |  |  |  |  |  |  | 2% | 2% |
| 9 |  |  |  |  |  |  | 3.8% | Not stated |
| 10 |  |  |  |  |  |  | 1.6% | 1.6% |
| 11 |  |  |  |  |  |  | 3.1% | 3.1% |
| 12 |  |  |  |  |  |  | 1.33% | .33% |
| 13 |  |  |  |  |  |  | 2% | 2% |
| THD24 |  |  |  |  |  |  | 23% | 13% |
| PWHD25 |  |  |  |  |  |  | 23% | 22% |
| Reason for not testing at 45-55% Registered Capacity (if applicable): |  |  |  |  |  |  |  |  |

—————————

- THD = Total Harmonic Distortion

- PWHD = Partial Weighted Harmonic Distortion

- THD = Total Harmonic Distortion

- PWHD = Partial Weighted Harmonic Distortion

| 3. Power Quality – Voltage fluctuations and Flicker: These tests should be undertaken in accordance with Annex A.7.2.5.3. Results should be normalised to a standard source impedance, or if this results in figures above the limits set in BS EN 61000-3-11 to a suitable maximum impedance. The standard test impedance is 0.4 Ω for a single phase Power Generating Module (and for a two phase unit in a three phase system) and 0.24 Ω for a three phase Power Generating Module (and for a two phase unit in a split phase system). Please ensure that both test and standard impedance are completed on this form. If the test impedance (or the measured impedance) is different to the standard impedance, it must be normalised to the standard impedance as follows (where the Power Factor of the generation output is 0.98 or above): d max normalised value = (Standard impedance / Measured impedance) x Measured value. Where the Power Factor of the output is under 0.98 then the X to R ratio of the test impedance should be close to that of the standard impedance. The stopping test should be a trip from full load operation. The duration of these tests needs to comply with the particular requirements set out in the testing notes for the technology under test. The test date and location must be declared. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Test start date |  |  |  |  |  |  | Test end date |  |  |  |  |  |  |  |
| Test location |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Starting |  |  |  |  | Stopping |  |  | Running |  |  |  |  |
|  |  | d max |  | d c | d(t) |  | d max |  | d c | d(t) |  |  | P st | P lt 2 hours |
| Measured Values at test impedance |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Normalised to standard impedance |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Normalised to required maximum impedance |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Limits set under BS EN 61000-3-11 |  | 4% |  | 3.3% | 3.3% |  | 4% |  | 3.3% | 3.3% |  |  | 1.0 | 0.65 |
| Test Impedance |  | R |  |  |  | Ω |  | X |  |  |  | Ω |  |  |
| Standard Impedance |  | R |  | 0.24 * 0.4 ^ |  | Ω |  | X |  |  | 0.15 * 0.25 ^ | Ω |  |  |
| Maximum Impedance |  | R |  |  |  | Ω |  | X |  |  |  | Ω |  |  |
| * Applies to three phase Power Generating Modules and split single phase Power Generating Modules. Delete as appropriate. ^ Applies to single phase Power Generating Module and Power Generating Modules using two phases on a three phase system. Delete as appropriate. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4. Power Factor: The tests should be carried out on a single Power Generating Module. Tests are to be carried out at three voltage levels and at Registered Capacity and the measured Power Factor must be greater than 0.95 to pass. Voltage to be maintained within ±1.5% of the stated level during the test. These tests should be undertaken in accordance with Annex A.7.2.5.2. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Voltage |  |  |  | 0.94 pu (216.2 V) |  |  |  | 1.0 pu (230 V) |  |  |  |  | 1.1 pu (253 V) |  |
| Measured value |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Power Factor Limit |  |  |  | >0.95 |  |  |  | >0.95 |  |  |  |  | >0.95 |  |
| 5. Protection – Frequency tests: These tests should be carried out in accordance with Annex A.7.2.2.3. For trip tests, frequency and time delay should be stated. For “no trip tests”, “no trip” can be stated. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Function | Setting |  |  |  |  | Trip test |  |  |  |  | “No trip tests” |  |  |  |
|  | Frequency |  |  | Time delay |  | Frequency |  | Time delay |  |  | Frequency /time |  | Confirm no trip |  |
| U/F stage 1 | 47.5 Hz |  |  | 20 s |  |  |  |  |  |  | 47.7 Hz 30 s |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 47.2 Hz 19.5 s |  |  |  |
| U/F stage 2 | 47 Hz |  |  | 0.5 s |  |  |  |  |  |  | 46.8 Hz 0.45 s |  |  |  |
| O/F | 52 Hz |  |  | 0.5 s |  |  |  |  |  |  | 51.8 Hz 120 s |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 52.2 Hz 0.45 s |  |  |  |

| 6. Protection – Voltage tests: These tests should be carried out in accordance with Annex A.7.2.2.2. For trip tests, voltage and time delay should be stated. For “no trip tests”, “no trip” can be stated. |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Function | Setting |  |  |  | Trip test |  |  |  | “No trip tests” |  |  |  |
|  | Voltage |  | Time delay |  | Voltage |  | Time delay |  | Voltage /time |  | Confirm no trip |  |
| U/V | 0.8 pu (184 V) |  | 2.5 s |  |  |  |  |  | 188 V 5.00 s |  |  |  |
|  |  |  |  |  |  |  |  |  | 180 V 2.45 s |  |  |  |
| O/V stage 1 | 1.14 pu (262.2 V) |  | 1.0 s |  |  |  |  |  | 258.2 V 5.0 s |  |  |  |
|  |  |  |  |  |  |  |  |  | 269.7 V 0.95s |  |  |  |
| O/V stage 2 | 1.19 pu (273.7 V) |  | 0.5 s |  |  |  |  |  | 277.7 V 0.45s |  |  |  |
| 7. Protection – Loss of Mains test: The tests are to be carried out at three output power levels ±5%. These tests should be carried out in accordance with Annex A.7.2.2.4. |  |  |  |  |  |  |  |  |  |  |  |  |
| To be carried out at three output power levels with a tolerance of ± 5% in Test Power levels.26 |  |  |  |  |  |  |  |  |  |  |  |  |
| Test Power (% of Registered Capacity) |  | 10% |  | 55% |  | 100% |  | 10% |  | 55% |  | 100% |
| Balancing load on islanded network |  | 95% of Test Power |  | 95% of Test Power |  | 95% of Test Power |  | 105% of Test Power |  | 105% of Test Power |  | 105% of Test Power |
| Trip time. Limit is 0.5 s |  |  |  |  |  |  |  |  |  |  |  |  |
| For Multi phase Power Generating Modules confirm that the device shuts down correctly after the removal of a single fuse as well as operation of all phases. |  |  |  |  |  |  |  |  |  |  |  |  |
| Test Power (% of Registered Capacity) |  | 10% |  | 55% |  | 100% |  | 10% |  | 55% |  | 100% |
| Balancing load on islanded network |  | 95% of Test Power |  | 95% of Test Power |  | 95% of Test Power |  | 105% of Test Power |  | 105% of Test Power |  | 105% of Test Power |
| Trip time. Ph1 fuse removed |  |  |  |  |  |  |  |  |  |  |  |  |
| Test Power (% of Registered Capacity) |  | 10% |  | 55% |  | 100% |  | 10% |  | 55% |  | 100% |

—————————

- See the note in A.7.2.2.4 if the suggested loading levels are below the Minimum Stable Operating Level. If alternative loading levels are chosen, the level should be indicated on the test form and the reason for not testing at 10%/55% of Registered Capacity should be stated in the box at the end of this section.

| Balancing load on islanded network | 95% of Test Power |  | 95% of Test Power |  | 95% of Test Power | 105% of Test Power |  | 105% of Test Power |  |  | 105% of Test Power |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Trip time. Ph2 fuse removed |  |  |  |  |  |  |  |  |  |  |  |
| Test Power (% of Registered Capacity) | 10% |  | 55% |  | 100% | 10% |  | 55% |  |  | 100% |
| Balancing load on islanded network | 95% of Test Power |  | 95% of Test Power |  | 95% of Test Power | 105% of Test Power |  | 105% of Test Power |  |  | 105% of Test Power |
| Trip time. Ph3 fuse removed |  |  |  |  |  |  |  |  |  |  |  |
| Note for technologies which have a substantial shut down time this can be added to the 0.5 s in establishing that the trip occurred in less than 0.5 s. Maximum shut down time could therefore be up to 1.0 s for these technologies. |  |  |  |  |  |  |  |  |  |  |  |
| Indicate additional shut down time included in above results. |  |  |  |  |  |  |  | ms |  |  |  |
| Reason for not testing at suggested loading levels (if applicable): |  |  |  |  |  |  |  |  |  |  |  |
| Loss of Mains Protection, Vector Shift Stability test: This test should be carried out in accordance with Annex A.7.2.2.6. Confirmation is required that the Power Generating Module does not trip under positive / negative vector shift. |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Start Frequency |  | Change |  |  | Confirm no trip |  |  |  |  |
| Positive Vector Shift |  | 49.5 Hz |  | +50 degrees |  |  |  |  |  |  |  |
| Negative Vector Shift |  | 50.5 Hz |  | - 50 degrees |  |  |  |  |  |  |  |
| Loss of Mains Protection, RoCoF Stability test: This test should be carried out in accordance with Annex A.7.2.2.6. Confirmation is required that the Power Generating Module does not trip for the duration of the ramp up and ramp down test. |  |  |  |  |  |  |  |  |  |  |  |
| Ramp range |  | Test frequency ramp: |  |  |  |  | Test Duration |  | Confirm no trip |  |  |
| 49.0Hz to 51.0Hz |  | +0.95 Hzs-1 |  |  |  |  | 2.1 s |  |  |  |  |
| 51.0Hz to 49.0Hz |  | -0.95 Hzs-1 |  |  |  |  | 2.1 s |  |  |  |  |
| 8. Limited Frequency Sensitive Mode – Overfrequency test: The test should be carried out using the specific threshold frequency of 50.4 Hz and Droop of 10%. This test should be carried out in accordance with Annex A.7.2.4. |  |  |  |  |  |  |  |  |  |  |  |
| Active Power response to rising frequency/time plots are attached |  |  |  |  |  |  |  |  |  | Y/N |  |

| 9. Power output with falling frequency test |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Tests should prove that the Power Generating Module does not reduce output power as the frequency falls. These tests should be carried out in accordance with Annex A.7.2.3. |  |  |  |  |  |  |  |  |
| Test sequence |  | Measured Active Power Output | Acceptable Active Power |  |  | Primary power source (if applicable) |  |  |
| 49.5 Hz for 5 minutes |  |  | 100% Registered Capacity |  |  |  |  |  |
| 49.0 Hz for 5 minutes |  |  | 99% Registered Capacity |  |  |  |  |  |
| 48.0 Hz for 5 minutes |  |  | 97% Registered Capacity |  |  |  |  |  |
| 47.6 Hz for 5 minutes |  |  | 96.2% Registered Capacity |  |  |  |  |  |
| 47.1 Hz for 20 s |  |  | 95% Registered Capacity |  |  |  |  |  |
| 10. Protection – Re-connection timer. |  |  |  |  |  |  |  |  |
| Test should prove that the reconnection sequence starts after a minimum delay of 20 s for restoration of voltage and frequency to within the stage 1 settings of Table 10.1. Both the time delay setting and the measured delay should be provided in this form; both should be greater than 20 s to pass. Confirmation should be provided that the Power Generating Module does not reconnect at the voltage and frequency settings below; a statement of “no reconnection” can be made. |  |  |  |  |  |  |  |  |
| Time delay setting | Measured delay | Checks on no reconnection when voltage or frequency is brought to just outside stage 1 limits of Table 10.1. |  |  |  |  |  |  |
|  |  | At 1.16 pu (266.2 V) |  | At 0.78 pu (180.0 V) | At 47.4 Hz |  | At 52.1 Hz |  |
| Confirmation that the Power Generating Module does not re- connect. |  |  |  |  |  |  |  |  |
| 11. Fault level contribution: Manufacturers’ Information in respect of the fault level contribution shall be provided. |  |  |  |  |  |  |  |  |
| 12. Wiring functional tests: If required by para 15.2.1, |  |  |  |  |  |  |  |  |
| Confirm that the relevant test schedule is attached (tests to be undertaken at time of commissioning) |  |  |  |  |  |  |  | Yes / NA |

| 13. Logic interface (input port) |  |
| --- | --- |
| Confirm that an input port is provided and can be used to shut down the module | Yes / NA |
| Provide high level description of logic interface, eg details in 11.1.3.1 such as AC or DC signal (the additional comments box below can be used) | Yes / NA |
| 14. Cyber security |  |
| Confirm that the Power Generating Module has been designed to comply with cyber security requirements, as detailed in 9.1.7. | Yes / NA |
| Additional comments |  |