| ## Form A3-2: Installation Notification Form for Small Generation Installation Procedures 2 and 3. Please complete and provide this document for each installation. Part 1 should be completed for the overall installation. Part 2 should be completed for each of the Generating Units (ie for the Electricity Storage devices and non-Electricity Storage Generating Unit Inverters) being commissioned. Where the installation is phased the form should be completed on a per Generating Unit basis as each part of the installation is completed in accordance with EREC G99 paragraph 15.3.3. For phased installations reference to PGM in this form should be read as reference to Generating Units. |  |
| --- | --- |
| Form A3-2 Part 1 |  |
| To ABC electricity distribution DNO 99 West St, Imaginary Town, ZZ99 9AA abced@wxyz.com |  |
| Generator details: |  |
| Generator (name) |  |
| Address |  |
| Post Code |  |
| Contact person (if different from Generator) |  |
| Telephone number |  |
| E-mail address |  |
| MPAN(s) |  |
| Generator signature |  |
| Installer details: |  |
| Installer |  |
| Accreditation / Qualification |  |
| Address |  |

| Post Code |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Contact person |  |  |  |  |  |  |  |  |  |  |
| Telephone Number |  |  |  |  |  |  |  |  |  |  |
| E-mail address |  |  |  |  |  |  |  |  |  |  |
| Installer signature |  |  |  |  |  |  |  |  |  |  |
| Installation details: |  |  |  |  |  |  |  |  |  |  |
| Address |  |  |  |  |  |  |  |  |  |  |
| Post code |  |  |  |  |  |  |  |  |  |  |
| Location within Generator’s Installation |  |  |  |  |  |  |  |  |  |  |
| Location of Lockable Isolation Switch |  |  |  |  |  |  |  |  |  |  |
| Summary details of Generating Units where multiple Generating Units will exist within one Generator’s Installation |  |  |  |  |  |  |  |  |  |  |
| Manufacturer / Reference | Date of Installation |  | Energy source and energy conversion technology (enter codes from tables 1 and 2 see Form A1-2) |  | Manufacturers Ref No. (system reference) or Reference to Form A2-3 | Generating Unit Registered Capacity in kW |  |  |  |  |
|  |  |  |  |  |  | 3- Phase Units | Single Phase Units |  |  | Power Factor |
|  |  |  |  |  |  |  | PH 1 | PH 2 | PH 3 |  |
|  |  |  | Src | Tech |  |  |  |  |  |  |
| Emerging technology classification (if applicable) |  |  |  |  |  |  |  |  |  |  |

| Commissioning checks |  |  |  |
| --- | --- | --- | --- |
| Description |  |  | Confirmation |
| Generator’s Installation satisfies the requirements of BS7671 (IET Wiring Regulations). |  |  | Yes / No* |
| Suitable lockable points of isolation have been provided between the PGM(s) and the rest of the Generator’s Installation. |  |  | Yes / No* |
| Labels have been installed at all points of isolation in accordance with EREC G99. |  |  | Yes / No* |
| Interlocking that prevents the PGM(s) being connected in parallel with the DNO’s Distribution Network (without synchronising) is in place and operates correctly. |  |  | Yes / No* |
| Balance of Multiple Single Phase PGM(s). Confirm that design of the Generator’s Installation has been carried out to limit output power imbalance to below 32 A per phase, as required by EREC G99. |  |  | Yes / No* |
| The PGM complies with cyber security requirements |  |  | Yes / No* |
| Export limitation scheme meets the requirements of EREC G100 and has been commissioned in accordance with EREC G100. |  |  | Yes / No* |
| Information to be enclosed |  |  |  |
| Description |  |  | Confirmation * |
| As installed Standard Application Form data, unless already provided. |  |  | Yes / No* |
| Final copy of circuit diagram |  |  | Yes / No* |
| EREC G100 Export limitation scheme installation and commissioning test form. |  |  | Yes / No* |
| Form A3-2 Part 2 |  |  |  |
| Power Generating Module reference or name |  |  |  |
| Information to be enclosed |  |  |  |
| Description |  | Confirmation * |  |
| Schedule of protection settings (may be included in circuit diagram) |  | Yes / No* |  |
| Commissioning checks |  |  |  |
| The Interface Protection settings have been checked and comply with EREC G99. |  | Yes / No* |  |
| The PGM successfully synchronises with the DNO’s Distribution Network without causing significant voltage disturbance. |  | Yes / No* |  |
| The PGM successfully runs in parallel with the DNO’s Distribution Network without tripping and without causing significant voltage disturbances. |  | Yes / No* |  |
| The PGM successfully disconnects without causing a significant voltage disturbance, when it is shut down. |  | Yes / No* |  |
| Interface Protection operates and disconnects the DNO’s Distribution Network quickly (within 1 s) when a suitably rated switch, located between the PGM and the DNO’s incoming connection, is opened. |  | Yes / No* |  |
| The PGM remains disconnected for at least 20 s after switch is reclosed. |  | Yes / No* |  |
| Loss of tripping and auxiliary supplies. Where applicable, loss of supplies to tripping and protection relays results in the forced trip of the PGM (or relevant Generating Unit) or an alarm to a 24 hour manned control centre. |  | Yes / No* |  |
| *Circle as appropriate. If “No” is selected the Power Generating Facility is deemed to have failed the commissioning tests and the PGM shall not be put in service. |  |  |  |
| Additional comments / observations: |  |  |  |

| Declaration – to be completed by Generator or Generator’s Appointed Technical Representative |  |
| --- | --- |
| I declare that for the Power Generating Module within the scope of this EREC G99, and the installation: - Compliance with the requirements of EREC G99 and EREC G100 is achieved. - The Power Generating Module is Fully Type Tested. - The commissioning checks detailed in this Form A3-2 Part 2 have been successfully completed. |  |
| Name: |  |
| Signature: | Date: |
| Company Name: |  |
| Position: |  |