- B.3	Installation and Commissioning Confirmation Form

| Form B3- Installation and Commissioning Confirmation Form for Type B PGMs Please complete and provide this document for every Power Generating Facility. Part 1 should be completed for the Power Generating Facility. Part 2 should be completed for each of the Power Generating Modules being commissioned. Where the installation is phased the form should be completed on a Generating Unit basis as each part of the installation is completed in accordance with EREC G99 paragraph 15.3.3. For phased installations reference to PGM in this form should be read as reference to Generating Units. |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Form B3 Part 1 |  |  |  |  |  |  |
| To ABC electricity distribution DNO 99 West St, Imaginary Town, ZZ99 9AA abced@wxyz.com |  |  |  |  |  |  |
| Installer or Generator Details: |  |  |  |  |  |  |
| Installer |  |  |  |  |  |  |
| Accreditation/Qualification |  |  |  |  |  |  |
| Address |  |  |  |  |  |  |
| Post Code |  |  |  |  |  |  |
| Contact person |  |  |  |  |  |  |
| Telephone Number |  |  |  |  |  |  |
| E-mail address |  |  |  |  |  |  |
| Installation Details: |  |  |  |  |  |  |
| Site Contact Details |  |  |  |  |  |  |
| Address |  |  |  |  |  |  |
| Post Code |  |  |  |  |  |  |
| Site Telephone Number |  |  |  |  |  |  |
| MPAN(s) |  |  |  |  |  |  |
| Location within Generator’s Installation |  |  |  |  |  |  |
| Location of Lockable Isolation Switch |  |  |  |  |  |  |
| Details of Power Generating Module(s): |  |  |  |  |  |  |
| Manufacturer / Reference | Date of Installation | Technology Type | Manufacturers Reference Number (system reference on ENA database) and or Equipment Certificate references as applicable |  | Power Generating Module |  |
|  |  |  |  |  | Registered Capacity in kW | Power Factor |
| Commissioning Checks: |  |  |  |  |  |  |
| Description |  |  |  | Confirmation |  |  |
| Generator’s Installation satisfies the requirements of BS7671 (IET Wiring Regulations). |  |  |  | Yes / No* |  |  |
| Suitable lockable points of isolation have been provided between the PGMs and the rest of the Generator’s Installation. |  |  |  | Yes / No* |  |  |
| Labels have been installed at all points of isolation in accordance with EREC G99. |  |  |  | Yes / No* |  |  |
| Interlocking that prevents the PGMs being connected in parallel with the DNO’s Distribution Network (without synchronising) is in place and operates correctly. |  |  |  | Yes / No* |  |  |
| PGM installation complies with cyber security requirements. |  |  |  | Yes / No* |  |  |
| Form B3 Part 2 |  |  |  |  |  |  |

| Power Generating Module reference or name |  |  |  |
| --- | --- | --- | --- |
| Information to be enclosed |  |  |  |
| Description |  |  | Confirmation |
| Final copy of circuit diagram. |  |  | Yes / No* |
| Schedule of protection settings (may be included in circuit diagram). |  |  | Yes / No* |
| Commissioning Checks |  |  |  |
| The Interface Protection settings have been checked and comply with EREC G99. |  |  | Yes / No / N/A (Type Tested)* |
| The PGM successfully synchronises with the DNO’s Distribution Network without causing significant voltage disturbance. |  |  | Yes / No* |
| The PGM successfully runs in parallel with the DNO’s Distribution Network without tripping and without causing significant voltage disturbances. |  |  | Yes / No* |
| The PGM successfully disconnects without causing a significant voltage disturbance, when it is shut down. |  |  | Yes / No* |
| Interface Protection operates and disconnects the PGM quickly (within 1s) when a suitably rated switch, located between the PGM and the DNO’s incoming connection, is opened. |  |  | Yes / No* |
| The PGM remains disconnected for at least 20s after switch is reclosed. |  |  | Yes / No* |
| Loss of tripping and auxiliary supplies. Where applicable, loss of supplies to tripping and protection relays results in either PGM or Generating Unit forced trip or an alarm to a 24 hour manned control centre. |  |  | Yes / No* |
| *Circle as appropriate. If “No” is selected the Power Generating Facility is deemed to have failed the commissioning tests and the Power Generating Module shall not be put in service. |  |  |  |
| Additional Comments / Observations: |  |  |  |
| Declaration – to be completed by Generator or Generators Appointed Technical Representative |  |  |  |
| I declare that for the Type B Power Generating Module within the scope of this EREC G99, and the installation: 1. The commissioning checks detailed in Form B2-2 have been successfully completed*. 2. The commissioning checks detailed in this Form B3 have been successfully completed. *delete if not applicable ie if the Interface Protection and ride through capabilities are Type Tested. |  |  |  |
| Name: |  |  |  |
| Signature: |  | Date: |  |
| Company |  |  |  |
| Position: |  |  |  |
| Declaration – to be completed by DNO Witnessing Representative |  |  |  |
| I confirm that I have witnessed: 1. The commissioning checks detailed in Form B2-2 *; 2. The commissioning checks detailed in this Form B3 and that the results are an accurate record of the checks. *delete if not applicable ie if the Interface Protection and ride through capabilities are Type Tested |  |  |  |
| Name: |  |  |  |
| Company Name |  |  |  |
| Signature: |  | Date: |  |