## P&C Equipment
Suitability | Supplier | Description | Model Number | Firmware/Software Version in use | Latest ENA assessed version | ENA NOC | SPEN Technical approval notice | Case Size | Additional Information | Nominal Current | Nominal Voltage | DC Supply
All | GE | Test terminal block without isolation pin in terminals 13 & 14 | MMLG02R1AA0001E |  |  | AN |  | 2 | Relay\IED Test Block | 1/5A
All | GE | Test terminal block with isolation pin in terminals 13 & 14 | MMLG012R1AB0001E |  |  | AN |  | 2 | Relay\IED Test Block | 1/5A
All | Siemens | Test terminal block without isolation pin in terminals 13 & 14 | 2RMLG-02 |  |  | AN |  | 2 | Busbar Protection\SPM AVC Test Block
All | Siemens | 7SJ82 Basic OCEF relay with single intertripping card for c37.94 communication | P1J1691498 | 9.71 Device 9.73 Comms | 9.71 | 245 |  | 1/3 x 19" | 4 x CT, 11 x BI, 7 x BO + WD, single I/T card | 1/5A | 63.5\110 | 110-250
All | Siemens | 7SJ82 Basic OCEF relay with single intertripping card for c37.94 communication | P1J1974713 | 9.71 Device 9.73 Comms | 9.71 | 245 |  | 1/3 x 19" | 4 x CT, 11 x BI, 7 x BO + WD, single I/T card | 1/5A | 63.5\110 | 24-48
All | Siemens | 7SJ82 Basic OCEF relay with dual intertripping card for c37.94 communication | P1J1789317 | 9.71 Device 9.73 Comms | 9.71 | 245 |  | 1/3 x 19" | 4 x CT, 11 x BI, 7 x BO + WD, dual I/T card | 1/5A | 63.5\110 | 110-250
All | Siemens | 7SJ82 Basic OCEF relay with dual intertripping card for c37.94 communication | P1J2094335 | 9.71 Device 9.73 Comms | 9.71 | 245 |  | 1/3 x 19" | 4 x CT, 11 x BI, 7 x BO + WD, dual I/T card | 1/5A | 63.5\110 | 24-48
All | Siemens | 7SD82 Differential Protection (single c37.94 card) | P1B381178 | 9.71 Device 9.73 Comms | 9.71 | 223 |  | 1/3 x 19" | 4 x CT, 4 x VT, 23 x BI, 15 x BO +WD | 1/5A | 63.5\110 | 110-250
All | Siemens | 7SD82 Differential Protection (single c37.94 card) | P1B385862 | 9.71 Device 9.73 Comms | 9.71 | 223 |  | 1/3 x 19" | 4 x CT, 4 x VT, 23 x BI, 15 x BO +WD | 1/5A | 63.5\110 | 24-48
All | Siemens | 7SD82 Differential Protection (dual c37.94 card) | P1B381987 | 9.71 Device 9.73 Comms | 9.71 | 223 |  | 1/3 x 19" | 4 x CT, 4 x VT, 23 x BI, 15 x BO +WD | 1/5A | 63.5\110 | 110-250
All | Siemens | 7SD82 Differential Protection (dual c37.94 card) | P1B406864 | 9.71 Device 9.73 Comms | 9.71 | 223 |  | 1/3 x 19" | 4 x CT, 4 x VT, 23 x BI, 15 x BO +WD | 1/5A | 63.5\110 | 24-48
All | Fundamentals | Supertapp SG Full CLASS enabled device | FP1034-AGG0000PDS-L06-30 |  |  | N/A |  |  | Not ENA assessed - Control Device. For information only.
All | Fundamentals | Supertapp SG CLASS ready chassis with basic AVC (normal requirement) | FP1034-AGG0000PDS-L06-10 |  |  | N/A |  |  | Not ENA assessed - Control Device. For information only.
All | Schneider | P541 Differential Protection for less than 910m direct / C37.94 | P541 211A1M0308J | 30 | 30 | 173 |  | 40TE | 4 x CT, 8 x BI , 7 x BO + WD | 1/5A | 110 | 110
All | Schneider | P541 Differential Protection for >1km, < 3.5 km direct (IDNO) | P541 211E1M0308J | 30 | 30 | 173 |  | 40TE | 4 x CT, 8 x BI , 7 x BO + WD | 1/5A | 110 | 110
All | Siemens | Bay Controller for LoM\Auto Changeover | P1J2538266 | 9.71 Device 9.73 Comms | 9.71 | 221
All | GE | C30 relay - single comms card single IO | C30-W00-HKH-F6S-HXX-MXX-PXX-UXX-W76 | 4.82 | Undergoing - 5.7 | 198 |  |  | If required for 30V / 48V site, the code will be HKL not HKH | 1/5A | 50\240 | 125-250
All | GE | C30 relay - double comms card single IO | C30-W00-HKH-F6S-HXX-MXX-PXX-UXX-W77 | 4.82 | Undergoing - 5.7 | 198 |  |  | If required for 30V / 48V site, the code will be HKL not HKH | 1/5A | 50\240 | 125-250
All | GE | C30 relay - single comms card double IO | C30-W00-HKH-F6S-H6S-MXX-PXX-UXX-W76 | 4.82 | Undergoing - 5.7 | 198 |  |  | If required for 30V / 48V site, the code will be HKL not HKH | 1/5A | 50\240 | 125-250
All | GE | C30 relay - double comms card double IO | C30-W00-HKH-F6S-H6X-MXX-PXX-UXX-W77 | 4.82 | Undergoing - 5.7 | 198 |  |  | If required for 30V / 48V site, the code will be HKL not HKH | 1/5A | 50\240 | 125-250
SPM | GE | Line Differential Protection (dual 850nm channel) - 2-3 ends | P543811A1S0910M | 91 |  | 116 |  |  | V91 undergoing ENA assessment
SPM | GE | Line Differential Protection (dual 850nm & 1300nm channel) | P543811H1S0910M | 91 |  | 116 |  |  | V91 undergoing ENA assessment
SPM | GE | Line Distance Protection | P443811A1S0910M | 71 |  | 128
SPM | GE | HV Back-up Protection (HSOC, TRR) | P141811N1S0910P | 91 |  | 101 |  |  | V91 undergoing ENA assessment
SPM | GE | LV Back-up Protection (OCEF, DAR, SYNCH, TRR) | P145811D1S0910M | 91 |  | 101 |  |  | V91 undergoing ENA assessment
SPM | Siemens | Transformer Differential Protection | 7SR5420-3AA22-0AA0 | 02.60.02/01.60 |  | TBA |  |  | Undergoing ENA assessment 21 BI, 10 BO, S8 enclosure
SPM | Siemens | Line Differential Protection - 7SD82 - 2-4 ends | P1B412650 | 8.83 | 9.71 | 223
SPM | Hitachi | Intertripping Device - single channel | NSD570-SP-G3LRa-C3794-110-30 |  |  | 131
SPM | Hitachi | Intertripping Device - double channel | 2 x NSD570-SP-C3794-G3LRa-110-30 |  |  | 131
SPM | GE | Operational Intertripping Device - Local | N60-U03-HLH-F8L-H6E-M8L-P6X-U8N-W77 | 8.5 |  | 199 |  |  | 4CT_2VT_8DI_22DO
SPM | GE | Operational Intertripping Device - Monitoring | N60-U03-HLH-F8L-H6W-M8L-P6X-U8L-W77 | 8.5 |  | 199 |  |  | 3CT_3VT_30DI_18DO
SPM | GE | Busbar Protection (Phase unit) | B90-U12-HKH-F8N-H67-L8N-N67-S8N-U67-W7H | 7.6 | 7.61 | 143
SPM | GE | Busbar Protection (Logic and CBF unit) | B90-U11-HLH-F6D-H6D-L6D-N6D-S6D-U67-W7H | 7.6 | 7.61 | 143
SPM/SPD | Schneider | Voltage protection relay including NVD | P5V20-AABB-DAAAA-AFEA | V01.500.104 | V01.500.104 | 238 |  |  | 4 x VT, 10 x BI, 7 x BO + WD |  | 63.5\110 | 110
SPM/SPD | Schneider | Pilot wire intertripping relay | GCM05 |  |  | AN54 | [5 empty] | 110
SPM/SPD | Schneider | Basic OCEF relay | P5U20-AABA-BAAAA-AFEA | V01.500.104 | V01.500.104 | 237 |  |  | 5 x CT, 4 x BI, 3 x BO + WD | 1/5A |  | 110
SPM/SPD | Siemens | High impedance busbar protection with CT supervision and IEC6180 electrical interface card | 7SR2302-1MA77-0CA0 | R8e-1c | R8e-1c | 184 |  | 6 | 4 x CT, 9 x BI. 8 x BO, 8 x LEDs | 1/5A | 63.5\110 | 110
SPM/SPD | Siemens | High impedance busbar protection with CT supervision and IEC6180 fibre interface card | 7SR2302-1MA87-0CA0 | R8e-1c | R8e-1c | 184 |  | 6 | 4 x CT, 9 x BI. 8 x BO, 8 x LEDs | 1/5A | 63.5\110 | 110
SPM/SPD | Siemens | High impedance busbar protection with CT supervision without IEC6180 fibre interface card | 7SR2302-1MA12-0CA0 | R8e-1c | R8e-1c | 184 |  | 6 | 4 x CT, 9 x BI. 8 x BO, 8 x LEDs | 1/5A | 63.5\110 | 110
SPM/SPD | Siemens | Backup protection and control unit for IEC61850 for distribution feeders type GP115 & GP2 V09.71 | P1J1754131 | 9.71 Device 9.73 Comms | 9.71 | 221 |  | 1/2 x 19" | 4 x CT, 4 x VT, 27 x BI, 17 x BO, single I/T card | 1/5A | 63.5\110 | 110
SPM/SPD | Siemens | Backup protection and control unit for IEC61850 distribution feeder type GT2 V09.71 | P1J1721942 | 9.71 Device 9.73 Comms | 9.71 | 221 |  | 1/2 x 19" | 4 x CT, 4 x VT, 27 x BI, 17 x BO | 1/5A | 63.5\110 | 110
SPM/SPD | Siemens | Backup protection and control unit for IEC61850 distribution feeder types (except GT2) V09.71 | P1J1754117 | 9.71 Device 9.73 Comms | 9.71 | 221 |  | 1/2 x 19" | 4 x CT, 4 x VT, 27 x BI, 17 x BO | 1/5A | 63.5\110 | 110
SPM/SPD | Siemens | SOLKOR RF pilot wire differential protection relay | 7PG2111-1DA30-0DB0 |  |  | AN |  |  |  | 1A
SPM/SPD | Siemens | Pilot supervision relay | 7PG2144-1CC40-1CE0 |  |  | AN | [5 empty] | 110
SPM/SPD | Siemens | Pilot supervision injection relay | 7PG2120-0AA00-1CA0 |  |  | AN |  |  |  |  | 110
SPM/SPD | Siemens | 7SA82 Distance Protection (single c37.94 card) | P1A645218 | 9.71 Device 9.73 Comms | 9.71 | 225 |  | 1/3 x 19" | 4 x CT, 4 x VT, 23 x BI, 15 x BO +WD | 1/5A | 63.5\110 | 110
SPM/SPD | Siemens | 7SA82 Distance Protection (single c37.94 card) | P1A679343 | 9.71 Device 9.73 Comms | 9.71 | 225 |  | 1/3 x 19" | 4 x CT, 4 x VT, 23 x BI, 15 x BO +WD | 1/5A | 63.5\110 | 24-48
SPM/SPD | Toshiba | Pilot wire\fibre differential protection relay | GRW200-11-1MG-12-LL-51-AA0-1051-LL1-1E |  |  | 235 |  |  |  | 1/5A | 63.5\110 | 110
SPM/SPD | Toshiba | Pilot wire differential protection relay | GRW200-11-1MG-11-LL-51-AA0-1051-LL1-1E |  |  | 235 |  |  |  | 1/5A | 63.5\110 | 110
SPM/SPD | Toshiba | Backup protection and control unit for IEC61850 all distribution feeder types | GRD200-41-F3T-00-LL-30-110-403D-LL2-FE |  |  | 217 |  | 1/2 x 19" | 5 x CT, 4 x VT, 30 x BI, 18 x BO | 1/5A | 63.5\110 | 110
SPM/SPD | Owen Brothers | Test terminal block for busbar protection CT short and disconnect | KP0023040 |  |  | AN |  | - | Part No. 4745 - CT Short & disconnect for busbar protection
SPM/SPD | Siemens | 7SR23 High imedance (REF) | 7PG23111DA301BA0 |  |  | 138 |  |  | 1 x CT, 2 x BO | 1/5A
SPM\SPD | GE | P541 Differential Protection | P541811A1S0300J | 30 | 83 | 116 |  | 40TE | 4 x CT, 8 x BI , 7 x BO + WD | 1/5A | 110 | 110
SPM\SPD | GE | P445 Distance Protection | P445811F1M0410P | 410 | 490 | 142 |  | 14 | 4 x CT, 4 x VT, 12 x BI, 12 x BO +WD | 1/5A | 35.5\110 | 110
SPM\SPD | GE | P14N non-directional basic OC & EF relay | P14NB11A1B0620A | 62 | 62 | 185 |  | 4 | 4 x CT, 8 x BI, 8 x BO | 1/5A | 63.5\110 | 24-250
SPM\SPD | GE | P14D directional basic OC & EF relay | P14DB11A330500A | 50 | 62 | 186 |  | 6 | 4 x CT, 4 x VT, 8 x BI, 8 x BO | 1/5A | 63.5\110 | 24-250
SPM\SPD | GE | P14N non-directional basic OC & EF relay (replacement for GAD relays) | P14NZ21C2C0500A | 50 | 62 | 185 |  | 6 | 4 x CT, 11 x BI, 12 x BO | 1/5A | 63.5\110 | 24-250
SPT | Hitachi | Differential Line Protection (2MP) | RED670 (1MRK002810-AG) | 2.2.5.11 | 2.2.2(hardware)/2.2.3.13(software) | 162 | [5 empty] | 110
SPT | GE | Differential Line Protection (1MP) - First Choice for 132kV/Standalone Distance Protection/Intertripping | P54581YA6T0910M | 91M | P54*8********M (hardware/0910D (software) | 116 |  |  | 24 inputs / 32 outputs. CH1 850nm multi mode - CH2 850nm multimode Dual LC ports |  |  | 110
SPT | GE | Differential Line Protection (1MP) - First Choice for 132kV/Standalone Distance Protection/Intertripping | P54581WA6T0910M | 91M | P54*8********M (hardware/0910D (software) | 116 |  |  | 24 inputs / 32 outputs. CH1 850nm multi mode - CH2 850nm multimode Dual RJ-45 ports
SPT | GE | Backup Protection (1st choice) TRR, DAR, SYNC, ANALOGUES, | P14381FM1T0910P | 91P | P14*8*****P (hardware)/91 (software) | 101 |  | 80TE | 32 input / 32 output |  |  | 110
SPT | GE | G99 Protection | P14381FM1T0910P | 91P | P14*8*****P (hardware)/91 (software) | 101 |  | 80TE | 32 input / 32 output |  |  | 110
SPT | GE | Dual Wound Transformer HSOC / 2ST HVOC | P14381FM1T0910P | 91P | P14*8*****P (hardware)/91 (software) | 101 |  | 80TE | 32 input / 32 output
SPT | GE | Dual Wound Transformer 2ST SBEF | P14NB16A6C0620A | 62 | P14N*****A(hardware)/62(software) | 185
SPT | GE | Dual Wound Transformer Overall Protection (2 winding) | P642811E3S0060P | P642_6_060_D | P642*****P(hardware)/091F (software) | 153 | [5 empty] | 110
SPT | GE | Dual Wound Transformer Overall Protection (3 winding) | P64381BG6S0060M | P643____6__060_D | P643*****M(hardware)/091F (software) | 153 | [5 empty] | 110
SPT | GE | High Impedance | MFAC14 |  |  | 137 | [5 empty] | 110
SPT | GE | High Impedance | MFAC34 |  |  | 137 | [5 empty] | 110
SPT | Siemens | Reactor Overall Protection | 7SR2303-1NA12-0CA0/CC |  | DAD 7SR230*-1*A**-0*A0 /CC (hardware) / 2435H85014R8e-1c(software) | 184 |  |  | Health Index of devices in our network is 3 |  |  | 110
SPT | GE | Load Management | N60-U03-HLH-F8L-H4D-M8L-P6W-U6X-W77 | 8.3 | - | 199 |  |  | Reported problems with communication card (W77) |  |  | 110
SPT | GE | Load Management /Intertripping (standalone first choice) | C30-U00-HLH-F6T-HXX-MXX-PXX-UXX-W77 | 4.82 | - | 198 |  |  | Version U00 not used before, Reported problems with communication card (W77) |  |  | 110
SPT | GE | Load Management | F60-U03-HLH-F8L-H4D-M8L-P6X-U6X-W77 | 8.5 |  |  |  |  | Not to be used until SPEN Assessment - Reported problems with communication card (W77) |  |  | 110
SPT | Hitachi | Mesh Corner DAR | REC670 (1MRK002814-AG) | 2.2.16.2 |  |  |  |  | Not to be used until SPEN Assessment |  |  | 110
SPT | Siemens | Low Impedance Busbar Protection | 7SS85 |  | 7.5 | 200 | [5 empty] | 110
SPT | ZIV | Low Impedance Busbar Protection | DBN (DBP/DBC) | DBPB4H221111FDA/DBCF5C2A4611NRA | DBC & DBP (harware) / ZivercomPlus® version 1.66 (software) | 191 | [5 empty] | 110
SPT | Siemens | Circuit Breaker Fail | 7SR1003-1KA20-2CA0 | [5 empty] | Not yet for use - Undergoing SPEN assessment |  |  | 110