## ADMD Calc (hidden)
ADMD Calc 3.68kW EVSE Only | [6 empty] | ADMD Calc 3.68kW Heat Pump Only
Customers | Mean | St Dev | St Dev % |  |  |  | Customers | Mean | St Dev | St Dev % |  | Increases at 50 customers (No Battery or PV) | ADMD | Addition vs Standard | % | 1.18 Factor due to differnce between EV HO and HP HO values from NPG | Increases at 1 customers (No Battery or PV) | ADMD | Addition vs Standard | % | Increases at 25 customers (No Battery or PV) | ADMD | Addition vs Standard | % | Increases at 75 customers (No Battery or PV) | ADMD | Addition vs Standard | % | Increases at 100 customers (No Battery or PV) | ADMD | Addition vs Standard | % | Variables | Options | Input
1 | 3.587 | 0.549 | 15.31% |  |  |  | 1 | 2.844 | 0.549 | 19.3% |  | House only | 1.929 | 0 | 0% |  | House only | 4.113 | 0 | 0% | House only | 1.799 | 0 | 0% | House only | 1.993 | 0 | 0% | House only | 2.066 | 0.137 | 0% | Number of Customers on Feeder ? | 1, 25, 50 or 100 | 50
25 | 3.756 | 0.021 | 0.5591% |  |  |  | 25 | 1.58 | 0.317 | 20.06% |  | With 3.68kW EVSE | 3.802 | 1.873 | 197.1% |  | With 3.68kW EVSE | 7.21 | 3.097 | 175.3% | With 3.68kW EVSE | 3.943 | 2.144 | 219.2% | With 3.68kW EVSE | 3.757 | 1.764 | 188.5% | With 3.68kW EVSE | 3.732 | 1.803 | 193.5% | Size of Charger ? | 0, 3.68 or 7.36 | 7.36
50 | 3.737 | 0.031 | 0.8295% |  |  |  | 50 | 1.389 | 0.192 | 13.82% |  | With 7.36kW (or two 3.68) EVSE | 5.4351 | 3.5061 | 281.8% |  | With 7.36kW (or two 3.68) EVSE | 10.307 | 6.194 | 250.6% | With 7.36kW (or two 3.68) EVSE | 5.6367 | 3.8377 | 313.3% | With 7.36kW (or two 3.68) EVSE | 5.3708 | 3.3778 | 269.5% | With 7.36kW (or two 3.68) EVSE | 5.3351 | 3.4061 | 276.6% | Heat Pump Installed ? | Yes or No | No
75 | 3.713 | 0.044 | 1.185% |  |  |  | 75 | 1.304 | 0.209 | 16.03% |  | With 3.68kW HP (10kW Heat Output) | 2.6043 | 0.67526 | 135% |  | With 3.68kW HP (10kW Heat Output) | 6.759 | 2.646 | 164.3% | With 3.68kW HP (10kW Heat Output) | 3.14 | 1.341 | 174.5% | With 3.68kW HP (10kW Heat Output) | 2.4166 | 0.42364 | 121.3% | With 3.68kW HP (10kW Heat Output) | 2.3364 | 0.4074 | 121.1% | Battery Storage ? | Yes or No | No
100 | 3.688 | 0.053 | 1.437% |  |  |  | 100 | 1.276 | 0.092 | 7.21% |  | With 3.68kW HP + 7.36kW EVSE | 5.8404 | 3.9114 | 302.8% |  | With 3.68kW HP + 7.36kW EVSE | 13.0369 | 8.9239 | 317% | With 3.68kW HP + 7.36kW EVSE | 6.5494 | 4.7504 | 364.1% | With 3.68kW HP + 7.36kW EVSE | 5.5899 | 3.5969 | 280.5% | With 3.68kW HP + 7.36kW EVSE | 5.4775 | 3.5485 | 284% | PV on Roof ? (Must have battery) | Yes or No | No
[33 empty] | Storage Heating Installed ? | Yes or No | No
[33 empty] | Extreme Outside Temp ? (T < - 5C) | Yes or No | Yes
[33 empty] | Is there a 60A current limitting device ? | Yes or No | No
ADMD Calc House only | [6 empty] | ADMD Calc 3.68kW HP + House |  |  |  |  | ADMD for 50 customers with Battery No PV | ADMD | Addition vs Standard | % |  | ADMD for 1 customers with Battery No PV | ADMD | Addition vs Standard | % | ADMD for 25 customers with Battery No PV | ADMD | Addition vs Standard | % | ADMD for 75 customers with Battery No PV | ADMD | Addition vs Standard | % | ADMD for 100 customers with Battery No PV | ADMD | Addition vs Standard | % |  | ADMD Normal Air Temp | 5.4351
Customers | Mean | St Dev | St Dev % |  |  |  | Customers | Mean | St Dev | St Dev % |  | House only | 1.93 | 0 | 0% |  | House only | 4.11 | 0 | 0% | House only | 1.8 | 0 | 0% | House only | 1.99 | 0 | 0% | House only | 2.07 | 0 | 0%
1 | 4.113 | 0.769 | 18.7% |  |  |  | 1 | 5.728 | 1.98 | 34.57% |  | With 3.68kWH Battery storage | 1.1574 | -0.7726 | 59.97% |  | With 3.68kWH Battery storage | 2.4678 | -1.6422 | 60.04% | With 3.68kWH Battery storage | 1.0794 | -0.7206 | 59.97% | With 3.68kWH Battery storage | 1.1934 | -0.79662 | 59.97% | With 3.68kWH Battery storage | 1.2396 | -0.8304 | 59.88% |  | ADMD Extreme Air Temp | 5.4351
25 | 1.799 | 0.343 | 19.07% |  |  |  | 25 | 2.661 | 0.673 | 25.29% |  | With 3.68kW EVSE + 3.68kWH Battery storage | 2.2812 | 0.3512 | 118.2% |  | With 3.68kW EVSE + 3.68kWH Battery storage | 4.326 | 0.216 | 105.3% | With 3.68kW EVSE + 3.68kWH Battery storage | 2.3658 | 0.5658 | 131.4% | With 3.68kW EVSE + 3.68kWH Battery storage | 2.5047 | 0.51473 | 125.9% | With 3.68kW EVSE + 3.68kWH Battery storage | 2.2392 | 0.1692 | 108.2%
50 | 1.929 | 0.358 | 18.56% |  |  |  | 50 | 2.207 | 0.387 | 17.54% |  | With 7.36kW EVSE + 3.68kWH Battery storage | 3.2611 | 1.3311 | 169% |  | With 7.36kW EVSE + 3.68kWH Battery storage | 6.1842 | 2.0742 | 150.5% | With 7.36kW EVSE + 3.68kWH Battery storage | 3.382 | 1.582 | 187.9% | With 7.36kW EVSE + 3.68kWH Battery storage | 3.5806 | 1.5906 | 179.9% | With 7.36kW EVSE + 3.68kWH Battery storage | 3.201 | 1.131 | 154.6% |  | ADMD Current Limiter | 5.4351
75 | 1.993 | 0.311 | 15.6% |  |  |  | 75 | 2.048 | 0.221 | 10.79% |  | With 3.68kW HP + 3.68kWH Battery storage | 1.5626 | -0.36744 | 80.96% |  | With 3.68kW HP + 3.68kWH Battery storage | 4.0554 | -0.054576 | 98.67% | With 3.68kW HP + 3.68kWH Battery storage | 1.884 | 0.083988 | 104.7% | With 3.68kW HP + 3.68kWH Battery storage | 1.6111 | -0.37887 | 80.96% | With 3.68kW HP + 3.68kWH Battery storage | 1.4018 | -0.66816 | 67.72%
100 | 2.066 | 0.229 | 11.08% |  |  |  | 100 | 1.98 | 0.128 | 6.465% |  | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage | 3.5179 | 1.5879 | 182.3% |  | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage | 7.8528 | 3.7428 | 191.1% | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage | 3.945 | 2.145 | 219.2% | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage | 3.7267 | 1.7367 | 187.3% | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage | 3.2994 | 1.2294 | 159.4%
ADMD Calc 3.68kW EVSE + House | [6 empty] | ADMD Calc 3.68kW HP + House + 7.36 kW EVSE |  |  |  |  | ADMD for 50 customers with Battery and PV | ADMD | Addition vs Standard | % |  | ADMD for 1 customers with Battery and PV | ADMD | Addition vs Standard | % | ADMD for 25 customers with Battery and PV | ADMD | Addition vs Standard | % | ADMD for 75 customers with Battery and PV | ADMD | Addition vs Standard | % | ADMD for 100 customers with Battery and PV | ADMD | Addition vs Standard | %
Customers | Mean | St Dev | St Dev % |  |  |  | Customers | Mean | St Dev | St Dev % | 1.18 Factor due to differnce between EV HO and HP HO values from NPG | House only | 1.93 | 0 | 0% |  | House only | 4.11 | 0 | 0% | House only | 1.8 | 0 | 0% | House only | 1.99 | 0 | 0% | House only | 2.07 | 0 | 0%
1 | 7.21 | 0.9 | 12.48% |  |  |  | 1 | 13.0369 | 3.0669 | 23.52% |  | With 3.68kWH Battery storage +3kW PV | 1.1227 | -0.80732 | 58.17% |  | With 3.68kWH Battery storage +3kW PV | 2.3938 | -1.7162 | 58.24% | With 3.68kWH Battery storage +3kW PV | 1.047 | -0.75298 | 58.17% | With 3.68kWH Battery storage +3kW PV | 0.63112 | -1.3589 | 31.71% | With 3.68kWH Battery storage +3kW PV | 1.2024 | -0.86759 | 60.42%
25 | 3.943 | 0.363 | 9.206% |  |  |  | 25 | 6.5494 | 1.1297 | 17.25% |  | With 3.68kW EVSE + 3.68kWH Battery storage + 3kW PV | 2.2128 | 0.28276 | 114.7% |  | With 3.68kW EVSE + 3.68kWH Battery storage + 3kW PV | 4.1962 | 0.08622 | 102.1% | With 3.68kW EVSE + 3.68kWH Battery storage + 3kW PV | 2.2948 | 0.49483 | 127.5% | With 3.68kW EVSE + 3.68kWH Battery storage + 3kW PV | 2.7886 | 0.79855 | 140.1% | With 3.68kW EVSE + 3.68kWH Battery storage + 3kW PV | 2.172 | 0.10202 | 109.1%
50 | 3.802 | 0.15 | 3.945% |  |  |  | 50 | 5.8404 | 0.62727 | 10.74% |  | With 7.36kW EVSE + 3.68kWH Battery storage + 3kW PV | 3.1632 | 1.2332 | 163.9% |  | With 7.36kW EVSE + 3.68kWH Battery storage + 3kW PV | 5.9987 | 1.8887 | 146% | With 7.36kW EVSE + 3.68kWH Battery storage + 3kW PV | 3.2806 | 1.4806 | 182.3% | With 7.36kW EVSE + 3.68kWH Battery storage + 3kW PV | 3.9864 | 1.9964 | 200.3% | With 7.36kW EVSE + 3.68kWH Battery storage + 3kW PV | 3.105 | 1.035 | 156%
75 | 3.757 | 0.087 | 2.316% |  |  |  | 75 | 5.5899 | 0.36632 | 6.553% |  | With 3.68kW HP + 3.68kWH Battery storage + 3kW PV | 1.5157 | -0.41432 | 78.53% | Same as C V33 | With 3.68kW HP + 3.68kWH Battery storage + 3kW PV | 3.9338 | -0.17624 | 95.71% | With 3.68kW HP + 3.68kWH Battery storage + 3kW PV | 1.8275 | 0.027468 | 101.5% | With 3.68kW HP + 3.68kWH Battery storage + 3kW PV | 1.7937 | -0.1963 | 90.14% | With 3.68kW HP + 3.68kWH Battery storage + 3kW PV | 1.3598 | -0.71022 | 68.33%
100 | 3.732 | 0.062 | 1.661% |  |  |  | 100 | 5.4775 | 0.22255 | 4.063% |  | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage +3kW PV | 3.4124 | 1.4824 | 176.8% |  | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage +3kW PV | 7.6172 | 3.5072 | 185.3% | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage +3kW PV | 3.8267 | 2.0267 | 212.6% | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage +3kW PV | 4.149 | 2.159 | 208.5% | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage +3kW PV | 3.2004 | 1.1304 | 160.8%
ADMD Calc 7.36kW EVSE + House
Customers | Mean | St Dev | St Dev % | [15 empty] | 1 coefficients |  |  |  | 25 coefficients |  |  |  | 75 coefficients |  |  |  | 100 coefficients
1 | 10.307 | 1.2866 | 12.48% | [15 empty] | 3.4275 |  |  |  | 1.4992 |  |  |  | 1.6608 |  |  |  | 1.7217
25 | 5.6367 | 0.51892 | 9.206% | [10 empty] | 50 coefficients |  |  |  | 1.753 | 1.0667 |  |  | 2.1918 | 1.2557 |  |  | 1.8851 | 1.5546 |  |  | 1.8064 | 1.5973
50 | 5.4351 | 0.21443 | 3.945% | [10 empty] | 1.6075 | Differnce in starting ADMD for Batt vs NPG Paper |  |  | 2.506 | 1.5249 |  |  | 3.1332 | 1.7951 |  |  | 2.6948 | 2.2224 |  |  | 2.5823 | 2.2834
75 | 5.3708 | 0.12437 | 2.316% | [9 empty] | 1.971 | 1.4599 | Ratio of EV 3.68 kW to HP kW for Cust |  |  | 1.6433 | 1.9288 |  |  | 1.7454 | 2.0858 |  |  | 1.2126 | 2.3131 |  |  | 1.1309 | 2.3444
100 | 5.3351 | 0.088632 | 1.661% | [9 empty] | 2.8176 | 2.087 | Ratio of EV 7.36 kW to HP kW for Cust |  |  | 3.1697 |  |  |  | 3.6406 |  |  |  | 2.8048 |  |  |  | 2.6512
[13 empty] | 1.3501 | 2.2426 | Ratio of EV 7.36 kW + HP kW to HPkW for Cust
3.0277
EV |  |  |  | HP | HP + EV |  | 0.84158 | DR Factor EV
3.097 | Diff House to 3.68EV | [6 empty] | DR Factor EV
1.8286 | R 1 to 25 |  |  | 2.1526 | 1.9906 | R 1 to 25
1.0371 | R 25 to 50 |  |  | 1.2057 | 1.1214 | R 25 to 50
1.012 | R 50 to 75 |  |  | 1.0776 | 1.0448 | R 50 to 75
1.0067 | R75 to 100 |  |  | 1.0343 | 1.0205 | R75 to 100
ADMD
-

## Variables Calc (hidden)
Equation Factors
Finding Value of Best Fit | X^ Value | Gradient |  |  | EV | HP | BS | PV | S
House only | 0.165 | 3.862 |  |  | 0.9 | 0.7 | 0.08 | 0.5 | 1.93
With 3.68kW EVSE | 0.15 | 7
With 7.36kW (or two 3.68) EVSE | 0.15 | 10 |  |  | Equipment Ratings
With 3.68kW HP (10kW Heat Output) | 0.236 | 6.723 |  |  | HP + BS + PV |  | EVSE
With 3.68kW HP + 7.36kW EVSE | 0.194 | 12.867 |  |  | 3.68 |  | 7.36
With 3.68kWH Battery storage | 0.164 | 1.67
With 3.68kW EVSE + 3.68kWH Battery storage | 0.078 | 4.92 |  |  | Overall Error
With 7.36kW EVSE + 3.68kWH Battery storage | 0.078 | 7.04 |  |  | 15.71% | Whole
With 3.68kW HP + 3.68kWH Battery storage | 0.164 | 4.73 |  |  | 14.46% | >25
With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage | 0.123 | 9.05
With 3.68kWH Battery storage +3kW PV | 0.167 | 1.23
With 3.68kW EVSE + 3.68kWH Battery storage + 3kW PV | 0.081 | 3.633
With 7.36kW EVSE + 3.68kWH Battery storage + 3kW PV | 0.081 | 5.194
With 3.68kW HP + 3.68kWH Battery storage + 3kW PV | 0.167 | 3.491
With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage +3kW PV | 0.125 | 6.678
Mean | 0.14153 | 5.8725
| Real | [6 empty] | Calculated |  |  |  |  | Error
Increases a customers Old Numbers | 100 | 75 | 50 | 25 | 1 |  |  | 100 | 75 | 50 | 25 | 1 | 100 | 75 | 50 | 25 | 1
House only | 2.066 | 1.993 | 1.929 | 1.799 | 4.113 |  |  | 1.93 | 1.93 | 1.93 | 1.93 | 1.93 | 6.583% | 3.161% | 0.05184% | 7.282% | 53.08%
With 3.68kW EVSE | 3.732 | 3.757 | 3.802 | 3.943 | 7.21 |  |  | 2.7317 | 2.8452 | 3.0133 | 3.3239 | 5.242 | 26.8% | 24.27% | 20.75% | 15.7% | 27.3%
With 7.36kW (or two 3.68) EVSE | 5.3351 | 5.3708 | 5.4351 | 5.6367 | 10.307 |  |  | 4.4576 | 4.6429 | 4.9171 | 5.4239 | 8.554 | 16.45% | 13.55% | 9.531% | 3.774% | 17.01%
With 3.68kW HP (10kW Heat Output) | 2.3364 | 2.4166 | 2.6043 | 3.14 | 6.759 |  |  | 2.3481 | 2.4457 | 2.5902 | 2.8572 | 4.506 | 0.5026% | 1.204% | 0.5406% | 9.007% | 33.33%
With 3.68kW HP + 7.36kW EVSE | 5.4989 | 5.6118 | 5.8632 | 6.575 | 13.088 |  |  | 5.8 | 6.041 | 6.3979 | 7.0573 | 11.13 | 5.475% | 7.649% | 9.118% | 7.335% | 14.96%
With 3.68kWH Battery storage | 0.90093 | 0.86611 | 0.84 | 0.78342 | 1.7888 |  |  | 0.85234 | 0.88776 | 0.94019 | 1.0371 | 1.6356 | 5.394% | 2.499% | 11.93% | 32.38% | 8.565%
With 3.68kW EVSE + 3.68kWH Battery storage | 4.0851 | 3.8223 | 3.4812 | 2.7926 | 5.4167 |  |  | 2.5783 | 2.6854 | 2.844 | 3.1372 | 4.9476 | 36.89% | 29.74% | 18.3% | 12.34% | 8.66%
With 7.36kW EVSE + 3.68kWH Battery storage | 5.8399 | 5.4641 | 4.9765 | 3.9922 | 7.7434 |  |  | 4.3042 | 4.4831 | 4.7479 | 5.2373 | 8.2596 | 26.3% | 17.95% | 4.595% | 31.19% | 6.666%
With 3.68kW HP + 3.68kWH Battery storage | 2.5575 | 2.4586 | 2.3845 | 2.2239 | 5.0779 |  |  | 2.1947 | 2.2859 | 2.421 | 2.6705 | 4.2116 | 14.18% | 7.025% | 1.528% | 20.08% | 17.06%
With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage | 6.0193 | 5.7093 | 5.3685 | 4.6568 | 9.8327 |  |  | 5.6466 | 5.8812 | 6.2286 | 6.8707 | 10.8356 | 6.192% | 3.011% | 16.02% | 47.54% | 10.2%
With 3.68kWH Battery storage +3kW PV | 0.65423 | 0.63112 | 0.62 | 0.56968 | 1.3203 |  |  | -0.10652 | -0.11094 | -0.1175 | -0.12961 | -0.2044 | 0% | 0% | 0% | 0% | 0%
With 3.68kW EVSE + 3.68kWH Battery storage + 3kW PV | 2.9701 | 2.7886 | 2.5695 | 2.0332 | 3.998 |  |  | 1.6194 | 1.6867 | 1.7863 | 1.9705 | 3.1076 | 45.48% | 39.51% | 30.48% | 3.084% | 22.27%
With 7.36kW EVSE + 3.68kWH Battery storage + 3kW PV | 4.2458 | 3.9864 | 3.6731 | 2.9065 | 5.7154 |  |  | 3.3453 | 3.4844 | 3.6902 | 4.0705 | 6.4196 | 21.21% | 12.59% | 0.4638% | 40.05% | 12.32%
With 3.68kW HP + 3.68kWH Battery storage + 3kW PV | 1.8594 | 1.7937 | 1.76 | 1.6191 | 3.748 |  |  | 1.8492 | 1.8386 | 1.8237 | 1.7986 | 1.6863 | 0.547% | 2.503% | 3.621% | 11.09% | 55.01%
With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage +3kW PV | 4.3763 | 4.1652 | 3.9625 | 3.3903 | 7.2575 |  |  | 4.6877 | 4.8825 | 5.1709 | 5.7039 | 8.9956 | 7.117% | 17.22% | 30.5% | 68.24% | 23.95%
|  |  | PV Additional Factor |  | 0.7381
Real
Increases a customers New Numbers | 100 | 75 | 50 | 25 | 1 |  |  |  | ADMD | Batt ADMD | Capacity | Charge Rate
House only | 2.066 | 1.993 | 1.929 | 1.799 | 4.113 |  |  | House | 2 | 1.2 | 6.03 | 0.98
With 3.68kW EVSE | 3.732 | 3.757 | 3.802 | 3.943 | 7.21 |  |  | With 3.68kW HP | 2.69 | 1.614 | 7.98 | 1.3
With 7.36kW (or two 3.68) EVSE | 5.3351 | 5.3708 | 5.4351 | 5.6367 | 10.307 |  |  | With 7.36kW EVSE | 5.64 | 3.384 | 17.25 | 2.8
With 3.68kW HP (10kW Heat Output) | 2.3364 | 2.4166 | 2.6043 | 3.14 | 6.759 |  |  | With 3.68kW HP + 7.36kW EVSE | 6.06 | 3.636 | 18.06 | 2.94
With 3.68kW HP + 7.36kW EVSE | 5.4989 | 5.6118 | 5.8632 | 6.575 | 13.088
With 3.68kWH Battery storage | 1.2396 | 1.1958 | 1.1574 | 1.0794 | 2.4678 |  |  | Relationships
With 3.68kW EVSE + Battery storage | 2.2392 | 2.2542 | 2.2812 | 2.3658 | 4.326 |  |  | Capacity to ADMD (kWh) | 3.015
With 7.36kW EVSE + Battery storage | 3.201 | 3.2225 | 3.2611 | 3.382 | 6.1842 |  |  | Charge Rate to ADMD (kW/h) | 0.49
With 3.68kW HP + Battery storage | 1.4018 | 1.45 | 1.5626 | 1.884 | 4.0554
With 3.68kW HP + 7.36kW EVSE + Battery storage | 3.2994 | 3.3671 | 3.5179 | 3.945 | 7.8528
With 3.68kWH Battery storage +3kW PV | 1.2024 | 1.1599 | 1.1227 | 1.047 | 2.3938
With 3.68kW EVSE + 3.68kWH Battery storage + 3kW PV | 2.172 | 2.1866 | 2.2128 | 2.2948 | 4.1962
With 7.36kW EVSE + 3.68kWH Battery storage + 3kW PV | 3.105 | 3.1258 | 3.1632 | 3.2806 | 5.9987
With 3.68kW HP + 3.68kWH Battery storage + 3kW PV | 1.3598 | 1.4065 | 1.5157 | 1.8275 | 3.9338
With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage +3kW PV | 3.2004 | 3.2661 | 3.4124 | 3.8267 | 7.6172
|  |  | PV Additional Factor |  | 0.97

## Batt. (hidden)
LCTs at Property |  |  | Battery Data |  | S = 14 kWh |  | LCTs at Property |  |  | Battery Data |  | S = 14 kWh |  | LCTs at Property |  |  | Battery Data |  | S = 14 kWh |  | LCTs at Property |  |  | Battery Data |  | S = 14 kwh
Standalone |  |  | Max Y = | 1.23 | C = 3.68 kW/h Max | D= 5kW/h Max | With Heat Pump |  |  | Max Y = | 1.64 | C = 3.68 kW/h Max | D= 5kW/h Max | With 7.36kW EVSE |  |  | Max Y = | 3.5 | C = 3.68 kW/h Max | D= 5kW/h Max | With 7.36kW EVSE + HP |  |  | Max Y = | 3.7 | C = 3.68 kW/h Max | D= 5kW/h Max
[7 empty] | 1.347 | [6 empty] | 2.82 | [6 empty] | 3.0276
Hour | Time | AHHD (G) | ADMD | Load | Available Charge (kWh) | Cuml. Batt Charge (kWh) | Hour | Time | AHHD (G) | ADMD | Load | Available Charge (kWh) | Cuml. Batt Charge (kWh) | Hour | Time | AHHD (G) | ADMD | Load | Available Charge (kWh) | Cuml. Batt Charge (kWh) | Hour | Time | AHHD (G) | ADMD | Load | Available Charge (kWh) | Cuml. Batt Charge (kWh)
0 | 0:00 | 0.1 | 0.25 | 1.23 | 0.98 | 0.98 | 0 | 0:00 | 0.1 | 0.33675 | 1.64 | 1.3032 | 1.3032 | 0 | 0:00 | 0.1 | 0.705 | 3.5 | 2.795 | 2.795 | 0 | 0:00 | 0.1 | 0.7569 | 3.7 | 2.9431 | 2.9431 | 3.7
1 | 1:00 | 0.2 | 0.5 | 1.23 | 0.73 | 1.71 | 1 | 1:00 | 0.2 | 0.6735 | 1.64 | 0.9665 | 2.2697 | 1 | 1:00 | 0.2 | 1.41 | 3.5 | 2.09 | 4.885 | 1 | 1:00 | 0.2 | 1.5138 | 3.7 | 2.1862 | 5.1293 | 3.7
2 | 2:00 | 0.15 | 0.375 | 1.23 | 0.855 | 2.565 | 2 | 2:00 | 0.15 | 0.50513 | 1.64 | 1.1349 | 3.4046 | 2 | 2:00 | 0.15 | 1.0575 | 3.5 | 2.4425 | 7.3275 | 2 | 2:00 | 0.15 | 1.1354 | 3.7 | 2.5647 | 7.694 | 3.7
3 | 3:00 | 0.15 | 0.375 | 1.23 | 0.855 | 3.42 | 3 | 3:00 | 0.15 | 0.50513 | 1.64 | 1.1349 | 4.5395 | 3 | 3:00 | 0.15 | 1.0575 | 3.5 | 2.4425 | 9.77 | 3 | 3:00 | 0.15 | 1.1354 | 3.7 | 2.5647 | 10.2586 | 3.7
4 | 4:00 | 0.15 | 0.375 | 1.23 | 0.855 | 4.275 | 4 | 4:00 | 0.15 | 0.50513 | 1.64 | 1.1349 | 5.6744 | 4 | 4:00 | 0.15 | 1.0575 | 3.5 | 2.4425 | 12.2125 | 4 | 4:00 | 0.15 | 1.1354 | 3.7 | 2.5647 | 12.8233 | 3.7
5 | 5:00 | 0.175 | 0.4375 | 1.23 | 0.7925 | 5.0675 | 5 | 5:00 | 0.175 | 0.58931 | 1.64 | 1.0507 | 6.7251 | 5 | 5:00 | 0.175 | 1.2337 | 3.5 | 2.2663 | 14.4787 | 5 | 5:00 | 0.175 | 1.3246 | 3.7 | 2.3754 | 15.1987 | 3.7
6 | 6:00 | 0.2 | 0.5 | 1.23 | 0.73 | 5.7975 | 6 | 6:00 | 0.2 | 0.6735 | 1.64 | 0.9665 | 7.6916 | 6 | 6:00 | 0.2 | 1.41 | 3.5 | 2.09 | 16.5687 | 6 | 6:00 | 0.2 | 1.5138 | 3.7 | 2.1862 | 17.3849 | 3.7
7 | 7:00 | 0.4 | 1 | 1.23 | 0.23 | 6.0275 | 7 | 7:00 | 0.4 | 1.347 | 1.64 | 0.293 | 7.9846 | 7 | 7:00 | 0.4 | 2.82 | 3.5 | 0.68 | 17.2487 | 7 | 7:00 | 0.4 | 3.0276 | 3.7 | 0.6724 | 18.0573 | 3.7 | PV Agg Input (kWh)
8 | 8:00 | 0.6 | 1.5 | 1.23 | -0.27 | 5.7575 | 8 | 8:00 | 0.6 | 2.0205 | 1.64 | -0.3805 | 7.6041 | 8 | 8:00 | 0.6 | 4.23 | 3.5 | -0.73 | 16.5187 | 8 | 8:00 | 0.6 | 4.5414 | 3.7 | -0.8414 | 17.2159 | 3.7 | 8:00 | 0.3
9 | 9:00 | 0.6 | 1.5 | 1.23 | -0.27 | 5.4875 | 9 | 9:00 | 0.6 | 2.0205 | 1.64 | -0.3805 | 7.2236 | 9 | 9:00 | 0.6 | 4.23 | 3.5 | -0.73 | 15.7887 | 9 | 9:00 | 0.6 | 4.5414 | 3.7 | -0.8414 | 16.3745 | 3.7 | 9:00 | 0.3
10 | 10:00 | 0.55 | 1.375 | 1.23 | -0.145 | 5.3425 | 10 | 10:00 | 0.55 | 1.8521 | 1.64 | -0.21213 | 7.0114 | 10 | 10:00 | 0.55 | 3.8775 | 3.5 | -0.3775 | 15.4112 | 10 | 10:00 | 0.55 | 4.163 | 3.7 | -0.46295 | 15.9115 | 3.7 | 10:00 | 0.3
11 | 11:00 | 0.5 | 1.25 | 1.23 | -0.02 | 5.3225 | 11 | 11:00 | 0.5 | 1.6837 | 1.64 | -0.04375 | 6.9677 | 11 | 11:00 | 0.5 | 3.525 | 3.5 | -0.025 | 15.3862 | 11 | 11:00 | 0.5 | 3.7845 | 3.7 | -0.0845 | 15.827 | 3.7 | 11:00 | 0.3
12 | 12:00 | 0.5 | 1.25 | 1.23 | -0.02 | 5.3025 | 12 | 12:00 | 0.5 | 1.6837 | 1.64 | -0.04375 | 6.9239 | 12 | 12:00 | 0.5 | 3.525 | 3.5 | -0.025 | 15.3612 | 12 | 12:00 | 0.5 | 3.7845 | 3.7 | -0.0845 | 15.7425 | 3.7 | 12:00 | 0.3
13 | 13:00 | 0.5 | 1.25 | 1.23 | -0.02 | 5.2825 | 13 | 13:00 | 0.5 | 1.6837 | 1.64 | -0.04375 | 6.8802 | 13 | 13:00 | 0.5 | 3.525 | 3.5 | -0.025 | 15.3362 | 13 | 13:00 | 0.5 | 3.7845 | 3.7 | -0.0845 | 15.658 | 3.7 | 13:00 | 0.3
14 | 14:00 | 0.5 | 1.25 | 1.23 | -0.02 | 5.2625 | 14 | 14:00 | 0.5 | 1.6837 | 1.64 | -0.04375 | 6.8364 | 14 | 14:00 | 0.5 | 3.525 | 3.5 | -0.025 | 15.3112 | 14 | 14:00 | 0.5 | 3.7845 | 3.7 | -0.0845 | 15.5735 | 3.7 | 14:00 | 0.3
15 | 15:00 | 0.5 | 1.25 | 1.23 | -0.02 | 5.2425 | 15 | 15:00 | 0.5 | 1.6837 | 1.64 | -0.04375 | 6.7927 | 15 | 15:00 | 0.5 | 3.525 | 3.5 | -0.025 | 15.2862 | 15 | 15:00 | 0.5 | 3.7845 | 3.7 | -0.0845 | 15.489 | 3.7 | 15:00 | 0.3
16 | 16:00 | 0.6 | 1.5 | 1.23 | -0.27 | 4.9725 | 16 | 16:00 | 0.6 | 2.0205 | 1.64 | -0.3805 | 6.4122 | 16 | 16:00 | 0.6 | 4.23 | 3.5 | -0.73 | 14.5562 | 16 | 16:00 | 0.6 | 4.5414 | 3.7 | -0.8414 | 14.6476 | 3.7 | 16:00 | 0.3
17 | 17:00 | 0.7 | 1.75 | 1.23 | -0.52 | 4.4525 | 17 | 17:00 | 0.7 | 2.3573 | 1.64 | -0.71725 | 5.6949 | 17 | 17:00 | 0.7 | 4.935 | 3.5 | -1.435 | 13.1212 | 17 | 17:00 | 0.7 | 5.2983 | 3.7 | -1.5983 | 13.0493 | 3.7 | Total PV contribution | 2.7
18 | 18:00 | 0.8 | 2 | 1.23 | -0.77 | 3.6825 | 18 | 18:00 | 0.8 | 2.694 | 1.64 | -1.054 | 4.6409 | 18 | 18:00 | 0.8 | 5.64 | 3.5 | -2.14 | 10.9812 | 18 | 18:00 | 0.8 | 6.0552 | 3.7 | -2.3552 | 10.6941 | 3.7 | Per Hour reduction (24H) | 0.1125
19 | 19:00 | 0.8 | 2 | 1.23 | -0.77 | 2.9125 | 19 | 19:00 | 0.8 | 2.694 | 1.64 | -1.054 | 3.5869 | 19 | 19:00 | 0.8 | 5.64 | 3.5 | -2.14 | 8.8412 | 19 | 19:00 | 0.8 | 6.0552 | 3.7 | -2.3552 | 8.3389 | 3.7 | New Threshold | 3.5875
20 | 20:00 | 0.8 | 2 | 1.23 | -0.77 | 2.1425 | 20 | 20:00 | 0.8 | 2.694 | 1.64 | -1.054 | 2.5329 | 20 | 20:00 | 0.8 | 5.64 | 3.5 | -2.14 | 6.7012 | 20 | 20:00 | 0.8 | 6.0552 | 3.7 | -2.3552 | 5.9837 | 3.7 | Percentage Total | 96.96%
21 | 21:00 | 0.8 | 2 | 1.23 | -0.77 | 1.3725 | 21 | 21:00 | 0.8 | 2.694 | 1.64 | -1.054 | 1.4789 | 21 | 21:00 | 0.8 | 5.64 | 3.5 | -2.14 | 4.5612 | 21 | 21:00 | 0.8 | 6.0552 | 3.7 | -2.3552 | 3.6285 | 3.7
22 | 22:00 | 0.6 | 1.5 | 1.23 | -0.27 | 1.1025 | 22 | 22:00 | 0.6 | 2.0205 | 1.64 | -0.3805 | 1.0984 | 22 | 22:00 | 0.6 | 4.23 | 3.5 | -0.73 | 3.8312 | 22 | 22:00 | 0.6 | 4.5414 | 3.7 | -0.8414 | 2.7871 | 3.7
23 | 23:00 | 0.4 | 1 | 1.23 | 0.23 | 1.3325 | 23 | 23:00 | 0.4 | 1.347 | 1.64 | 0.293 | 1.3914 | 23 | 23:00 | 0.4 | 2.82 | 3.5 | 0.68 | 4.5112 | 23 | 23:00 | 0.4 | 3.0276 | 3.7 | 0.6724 | 3.4595 | 3.7
[5 empty] | % Peak Shaved | 38.5% | [5 empty] | % Peak Shaved | 39.12% | [5 empty] | % Peak Shaved | 37.94% | [5 empty] | % Peak Shaved | 38.9%
[5 empty] | Capacity Needed | 6.0275 | [5 empty] | Capacity Needed | 7.9846 | [5 empty] | Capacity Needed | 17.2487 | [5 empty] | Capacity Needed | 18.0573
[5 empty] | Max Charge Rate | 0.98 | [5 empty] | Max Charge Rate | 1.3032 | [5 empty] | Max Charge Rate | 2.795 | [5 empty] | Max Charge Rate | 2.9431
[5 empty] | Max Discharge Rate | -0.77 | [5 empty] | Max Discharge Rate | -1.054 | [5 empty] | Max Discharge Rate | -2.14 | [5 empty] | Max Discharge Rate | -2.3552
Cs = 50
[7 empty] | LCTs at Property |  |  | Battery Data |  | S = 14 kWh |  | LCTs at Property |  |  | Battery Data |  | S = 14 kWh | V 2 G | LCTs at Property |  |  | Battery Data |  | S = 14 kwh | V 2 G
[7 empty] | With Heat Pump |  |  | Y= | 5.2 | C = 3.68 kW/h Max | D= 5kW/h Max | With 7.36kW EVSE |  |  | Y= | 3 | C = 3.68 kW/h Max | D= 5kW/h Max | With 7.36kW EVSE + HP |  |  | Y= | 3.7 | C = 3.68 kW/h Max | D= 5kW/h Max
[7 empty] | 4.207 | [6 empty] | 2.82 | [6 empty] | 3.0276
[7 empty] | Hour | Time | AHHD (G) | ADMD | Load | Available Charge (kWh) | Cuml. Batt Charge (kWh) | Hour | Time | AHHD (G) | ADMD | Load | Available Charge (kWh) | Cuml. Batt Charge (kWh) | Hour | Time | AHHD (G) | ADMD | Load | Available Charge (kWh) | Cuml. Batt Charge (kWh)
[7 empty] | 0 | 0:00 | 0.1 | 1.0517 | 5.2 | 4.1482 | 4.1482 | 0 | 0:00 | 0.1 | 0.705 | 3 | 2.295 | 2.295 | 0 | 0:00 | 0.1 | 0.7569 | 3.7 | 2.9431 | 2.9431
[7 empty] | 1 | 1:00 | 0.2 | 2.1035 | 5.2 | 3.0965 | 8.6362 | 1 | 1:00 | 0.2 | 1.41 | 3 | 1.59 | 3.885 | 1 | 1:00 | 0.2 | 1.5138 | 3.7 | 2.1862 | 5.1293
[7 empty] | 2 | 2:00 | 0.15 | 1.5776 | 5.2 | 3.6224 | 12.2586 | 2 | 2:00 | 0.15 | 1.0575 | 3 | 1.9425 | 5.8275 | 2 | 2:00 | 0.15 | 1.1354 | 3.7 | 2.5647 | 7.694
[7 empty] | 3 | 3:00 | 0.15 | 1.5776 | 5.2 | 3.6224 | 15.8809 | 3 | 3:00 | 0.15 | 1.0575 | 3 | 1.9425 | 7.77 | 3 | 3:00 | 0.15 | 1.1354 | 3.7 | 2.5647 | 10.2586
[7 empty] | 4 | 4:00 | 0.15 | 1.5776 | 5.2 | 3.6224 | 19.5033 | 4 | 4:00 | 0.15 | 1.0575 | 3 | 1.9425 | 9.7125 | 4 | 4:00 | 0.15 | 1.1354 | 3.7 | 2.5647 | 12.8233
[7 empty] | 5 | 5:00 | 0.175 | 1.8406 | 5.2 | 3.3594 | 22.8627 | 5 | 5:00 | 0.175 | 1.2337 | 3 | 1.7663 | 11.4787 | 5 | 5:00 | 0.175 | 1.3246 | 3.7 | 2.3754 | 15.1987
[7 empty] | 6 | 6:00 | 0.2 | 2.1035 | 5.2 | 3.0965 | 25.9592 | 6 | 6:00 | 0.2 | 1.41 | 3 | 1.59 | 13.0687 | 6 | 6:00 | 0.2 | 1.5138 | 3.7 | 2.1862 | 17.3849
[7 empty] | 7 | 7:00 | 0.4 | 4.207 | 5.2 | 0.993 | 26.9522 | 7 | 7:00 | 0.4 | 2.82 | 3 | 0.18 | 13.2487 | 7 | 7:00 | 0.4 | 3.0276 | 3.7 | 0.6724 | 18.0573
[7 empty] | 8 | 8:00 | 0.6 | 6.3105 | 5.2 | -1.1105 | 25.8418 | 8 | 8:00 | 0.6 | 4.23 | 4.23 | 0 | N/A | 8 | 8:00 | 0.6 | 4.5414 | 3.7 | -0.8414 | 17.2159
[7 empty] | 9 | 9:00 | 0.6 | 6.3105 | 5.2 | -1.1105 | 24.7313 | 9 | 9:00 | 0.6 | 4.23 | 4.23 | 0 | N/A | 9 | 9:00 | 0.6 | 4.5414 | 3.7 | -0.8414 | 16.3745
[7 empty] | 10 | 10:00 | 0.55 | 5.7846 | 5.2 | -0.58462 | 24.1466 | 10 | 10:00 | 0.55 | 3.8775 | 3.8775 | 0 | N/A | 10 | 10:00 | 0.55 | 4.163 | 3.7 | -0.46295 | 15.9115
[7 empty] | 11 | 11:00 | 0.5 | 5.2588 | 5.2 | -0.05875 | 24.0879 | 11 | 11:00 | 0.5 | 3.525 | 3.525 | 0 | N/A | 11 | 11:00 | 0.5 | 3.7845 | 3.7 | -0.0845 | 15.827
[7 empty] | 12 | 12:00 | 0.5 | 5.2588 | 5.2 | -0.05875 | 24.0291 | 12 | 12:00 | 0.5 | 3.525 | 3.525 | 0 | N/A | 12 | 12:00 | 0.5 | 3.7845 | 3.7 | -0.0845 | 15.7425
[7 empty] | 13 | 13:00 | 0.5 | 5.2588 | 5.2 | -0.05875 | 23.9704 | 13 | 13:00 | 0.5 | 3.525 | 3.525 | 0 | N/A | 13 | 13:00 | 0.5 | 3.7845 | 3.7 | -0.0845 | 15.658
[7 empty] | 14 | 14:00 | 0.5 | 5.2588 | 5.2 | -0.05875 | 23.9116 | 14 | 14:00 | 0.5 | 3.525 | 3.525 | 0 | N/A | 14 | 14:00 | 0.5 | 3.7845 | 3.7 | -0.0845 | 15.5735
[7 empty] | 15 | 15:00 | 0.5 | 5.2588 | 5.2 | -0.05875 | 23.8529 | 15 | 15:00 | 0.5 | 3.525 | 3.525 | 0 | N/A | 15 | 15:00 | 0.5 | 3.7845 | 3.7 | -0.0845 | 15.489
[7 empty] | 16 | 16:00 | 0.6 | 6.3105 | 5.2 | -1.1105 | 22.7424 | 16 | 16:00 | 0.6 | 4.23 | 4.23 | 0 | N/A | 16 | 16:00 | 0.6 | 4.5414 | 3.7 | -0.8414 | 14.6476
[7 empty] | 17 | 17:00 | 0.7 | 7.3622 | 5.2 | -2.1622 | 20.5801 | 17 | 17:00 | 0.7 | 4.935 | 4.935 | 0 | N/A | 17 | 17:00 | 0.7 | 5.2983 | 3.7 | -1.5983 | 13.0493
[7 empty] | 18 | 18:00 | 0.8 | 8.414 | 5.2 | -3.214 | 17.3661 | 18 | 18:00 | 0.8 | 5.64 | 5.64 | 0 | N/A | 18 | 18:00 | 0.8 | 6.0552 | 3.7 | -2.3552 | 10.6941
[7 empty] | 19 | 19:00 | 0.8 | 8.414 | 5.2 | -3.214 | 14.1521 | 19 | 19:00 | 0.8 | 5.64 | 3 | -2.64 | 10.6088 | 19 | 19:00 | 0.8 | 6.0552 | 3.7 | -2.3552 | 8.3389
[7 empty] | 20 | 20:00 | 0.8 | 8.414 | 5.2 | -3.214 | 10.9381 | 20 | 20:00 | 0.8 | 5.64 | 3 | -2.64 | 7.9688 | 20 | 20:00 | 0.8 | 6.0552 | 3.7 | -2.3552 | 5.9837
[7 empty] | 21 | 21:00 | 0.8 | 8.414 | 5.2 | -3.214 | 7.7241 | 21 | 21:00 | 0.8 | 5.64 | 3 | -2.64 | 5.3288 | 21 | 21:00 | 0.8 | 6.0552 | 3.7 | -2.3552 | 3.6285
[7 empty] | 22 | 22:00 | 0.6 | 6.3105 | 5.2 | -1.1105 | 6.6136 | 22 | 22:00 | 0.6 | 4.23 | 3 | -1.23 | 4.0988 | 22 | 22:00 | 0.6 | 4.5414 | 3.7 | -0.8414 | 2.7871
[7 empty] | 23 | 23:00 | 0.4 | 4.207 | 5.2 | 0.993 | 7.6066 | 23 | 23:00 | 0.4 | 2.82 | 3 | 0.18 | 4.2788 | 23 | 23:00 | 0.4 | 3.0276 | 3.7 | 0.6724 | 3.4595
[12 empty] | % Peak Shaved | 38.2% | [5 empty] | % Peak Shaved | 0% | [5 empty] | % Peak Shaved | 38.9%
[12 empty] | Capacity Needed | 26.9522 | [5 empty] | Capacity Needed | 13.2487 | [5 empty] | Capacity Needed | 18.0573
[12 empty] | Max Charge Rate | 4.1482 | [5 empty] | Max Charge Rate | 2.295 | [5 empty] | Max Charge Rate | 2.9431
[12 empty] | Max Discharge Rate | -3.214 | [5 empty] | Max Discharge Rate | -2.64 | [5 empty] | Max Discharge Rate | -2.3552

## Curr Lim. (hidden)
| KVA | Amps |  | Amps->kVA | KVA-> Amps |  |  |  | Note: | [5 empty] | Notes:
House demand (60A fuse) | 4.11 | 17.8696 |  | 0.23 | 4.3478 |  |  |  | all instances use the fast EV as this is the worst case scenario | [5 empty] | If the limiter is in affect the, ADMD will decrease the same percentage as the current
House demand (80A fuse) | 4.11 | 17.8696 | [12 empty] | 80 and 100 amp limiters have negligible affects on ADMD as the current does not reach these limits
House demand (100A fuse) | 4.11 | 17.8696 | [12 empty] | Only breach the 60 Amp limit when there is only 1 customer on the feeder
EV (slow charger) | 3.86 | 16.7826 |  |  |  | Amps | KVA |  |  | Amps | KVA |  |  |  | This result indicates that some LCT would be need to beswitched off (knocked out, most likely EV) might need to reflect the switching heiracrchy in the equation
EV (fast charger) | 7.36 | 32 |  | Panasonic HP | Normal | 11 | 2.53 |  | current limit | 60 | 13.8 |  |  |  | Also I think it is a believeable result as the original ADMD is over the threshold therefore the new ADMD is at the limit set by the current limiter
HP | 12 | 52.1739 |  |  | Extreme | 29 | 6.67 |  |  | 80 | 18.4
BES | 3.6 | 15.6522 | [7 empty] | 100 | 23
PV | 3.6 | 15.6522 | [12 empty] | For 1 customer:
test | 21.8 | 94.7826
| 60A fuse | House | House + EV | House + 2EV | House + Pan HP | House + Pan HP + EV | House + Pan HP + EV + PV | House + Pan HP + EV + BES | House + Pan HP + EV + BES + PV | House + Pan HP Extr | House + Pan HP Extr + EV | House + Pan HP Extr + EV + PV | House + Pan HP Extr + EV + BES | House + Pan HP Extr + EV + BES + PV | 60A Current limiter | House | House + EV | House + 2EV | House + Pan HP | House + Pan HP + EV | House + Pan HP + EV + PV | House + Pan HP + EV + BES | House + Pan HP + EV + BES + PV | House + Pan HP Extr | House + Pan HP Extr + EV | House + Pan HP Extr + EV + PV | House + Pan HP Extr + EV + BES | House + Pan HP Extr + EV + BES + PV
| Load (KVA) | 4.11 | 4.11 | 4.11 | 4.11 | 4.11 | 4.11 | 4.11 | 4.11 | 4.11 | 4.11 | 4.11 | 7 | 4.11 | ADMD from Calc | 4.11 | 7.21 | 10.31 | 6.76 | 13.04 | N/A | 9.79 | 7.23 | 12.28 | 18.56 | N/A | 15.31 | 12.75
| Additional Load (KVA) | 0 | 7.36 | 14.72 | 2.53 | 9.89 | 6.29 | 6.29 | 2.69 | 6.67 | 14.03 | 10.43 | 7 | 6.83 | Total Load Amps | 17.8696 | 31.3478 | 44.8261 | 29.3913 | 56.6957 | #VALUE! | 42.5652 | 31.4348 | 53.3913 | 80.6957 | #VALUE! | 66.5652 | 55.4348
| Total Load kVA | 4.11 | 11.47 | 18.83 | 6.64 | 14 | 10.4 | 10.4 | 6.8 | 10.78 | 18.14 | 14.54 | 14 | 10.94 | Percentage Over limiter | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 25.65% | N/A | 9.863% | N/A
| Total Load Amps | 17.8696 | 49.8696 | 81.8696 | 28.8696 | 60.8696 | 45.2174 | 45.2174 | 29.5652 | 46.8696 | 78.8696 | 63.2174 | 60.8696 | 47.5652 | ADMD | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 13.8 | N/A | 13.8 | N/A
| ADMD from Calc | 4.11 | 7.21 | 10.31 | 6.76 | 13.04 | N/A | 9.79 | 7.23 | 12.28 | 18.56 | N/A | 15.31 | 12.75
| Total Load Amps | 17.8696 | 31.3478 | 44.8261 | 29.3913 | 56.6957 | #VALUE! | 42.5652 | 31.4348 | 53.3913 | 80.6957 | #VALUE! | 66.5652 | 55.4348
For 25 Customers:
| 80A fuse | House | House + EV | House + 2EV | House + Pan HP | House + Pan HP + EV | House + Pan HP + EV + PV | House + Pan HP + EV + BES | House + Pan HP + EV + BES + PV | House + Pan HP Extr | House + Pan HP Extr + EV | House + Pan HP Extr + EV + PV | House + Pan HP Extr + EV + BES | House + Pan HP Extr + EV + BES + PV | 60A Current limiter | House | House + EV | House + 2EV | House + Pan HP | House + Pan HP + EV | House + Pan HP + EV + PV | House + Pan HP + EV + BES | House + Pan HP + EV + BES + PV | House + Pan HP Extr | House + Pan HP Extr + EV | House + Pan HP Extr + EV + PV | House + Pan HP Extr + EV + BES | House + Pan HP Extr + EV + BES + PV
| Load (KVA) | 4.11 | 4.11 | 4.11 | 4.11 | 4.11 | 4.11 | 4.11 | 4.11 | 4.11 | 4.11 | 4.11 | 4.11 | 4.11 | ADMD from Calc | 1.8 | 3.94 | 5.64 | 3.14 | 6.55 | N/A | 4.64 | 3.38 | 8.66 | 12.07 | N/A | 10.16 | 8.9
| Additional Load (KVA) | 0 | 7.36 | 14.72 | 2.53 | 9.89 | 6.29 | 6.29 | 2.69 | 6.67 | 14.03 | 10.43 | 10.43 | 6.83 | Total Load Amps | 7.8261 | 17.1304 | 24.5217 | 13.6522 | 28.4783 | #VALUE! | 20.1739 | 14.6957 | 37.6522 | 52.4783 | #VALUE! | 44.1739 | 38.6957
| Total Load kVA | 4.11 | 11.47 | 18.83 | 6.64 | 14 | 10.4 | 10.4 | 6.8 | 10.78 | 18.14 | 14.54 | 14.54 | 10.94 | Percentage Over limiter | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | -14.33% | N/A | -35.83% | N/A
| Total Load Amps | 17.8696 | 49.8696 | 81.8696 | 28.8696 | 60.8696 | 45.2174 | 45.2174 | 29.5652 | 46.8696 | 78.8696 | 63.2174 | 63.2174 | 47.5652 | ADMD | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 13.8 | N/A | 13.8 | N/A
| ADMD from Calc | 4.11 | 7.21 | 10.31 | 6.76 | 13.04 | N/A | 9.79 | 7.23 | 12.28 | 18.56 | N/A | 15.31 | 12.75
| Total Load Amps | 17.8696 | 31.3478 | 44.8261 | 29.3913 | 56.6957 | #VALUE! | 42.5652 | 31.4348 | 53.3913 | 80.6957 | #VALUE! | 66.5652 | 55.4348
| 100A fuse | House | House + EV | House + 2EV | House + Pan HP | House + Pan HP + EV | House + Pan HP + EV + PV | House + Pan HP + EV + BES | House + Pan HP + EV + BES + PV | House + Pan HP Extr | House + Pan HP Extr + EV | House + Pan HP Extr + EV + PV | House + Pan HP Extr + EV + BES | House + Pan HP Extr + EV + BES + PV
| Load (KVA) | 4.11 | 4.11 | 4.11 | 4.11 | 4.11 | 4.11 | 4.11 | 4.11 | 4.11 | 4.11 | 4.11 | 4.11 | 4.11
| Additional Load (KVA) | 0 | 7.36 | 14.72 | 2.53 | 9.89 | 6.29 | 6.29 | 2.69 | 6.67 | 14.03 | 10.43 | 10.43 | 6.83
| Total Load kVA | 4.11 | 11.47 | 18.83 | 6.64 | 14 | 10.4 | 10.4 | 6.8 | 10.78 | 18.14 | 14.54 | 14.54 | 10.94
| Total Load Amps | 17.8696 | 49.8696 | 81.8696 | 28.8696 | 60.8696 | 45.2174 | 45.2174 | 29.5652 | 46.8696 | 78.8696 | 63.2174 | 63.2174 | 47.5652
| ADMD from Calc | 4.11 | 7.21 | 10.31 | 6.76 | 13.04 | N/A | 9.79 | 7.23 | 12.28 | 18.56 | N/A | 15.31 | 12.75
| Total Load Amps | 17.8696 | 31.3478 | 44.8261 | 29.3913 | 56.6957 | #VALUE! | 42.5652 | 31.4348 | 53.3913 | 80.6957 | #VALUE! | 66.5652 | 55.4348

## HPC5N (hidden)
ADMD Calc 3.68kW EVSE Only | [6 empty] | ADMD Calc 3.68kW Heat Pump Only (obselete)
Customers | Mean | St Dev | St Dev % |  |  |  | Customers | Mean | St Dev | St Dev % |  |  |  | Increases at 50 customers (No Battery or PV) | ADMD | Addition vs Standard | % | 1.18 Factor due to differnce between EV HO and HP HO values from NPG (Negated by HP Peak in monring) | Increases at 1 customers (No Battery or PV) | ADMD | Addition vs Standard | % | Increases at 25 customers (No Battery or PV) | ADMD | Addition vs Standard | % | Increases at 75 customers (No Battery or PV) | ADMD | Addition vs Standard | % | Increases at 100 customers (No Battery or PV) | ADMD | Addition vs Standard | % | Variables | Options | Input
1 | 3.587 | 0.549 | 15.31% |  |  |  | 1 | 2.844 | 0.549 | 19.3% |  |  |  | House only | 1.929 | 0 | 0% |  | House only | 4.113 | 0 | 0% | House only | 1.799 | 0 | 0% | House only | 1.993 | 0 | 0% | House only | 2.066 | 0.137 | 0% | Number of Customers on Feeder ? | 1, 25, 50 or 100 | 25
25 | 3.756 | 0.021 | 0.5591% |  |  |  | 25 | 1.58 | 0.317 | 20.06% |  |  |  | With 3.68kW EVSE | 3.802 | 1.873 | 197.1% |  | With 3.68kW EVSE | 7.21 | 3.097 | 175.3% | With 3.68kW EVSE | 3.943 | 2.144 | 219.2% | With 3.68kW EVSE | 3.757 | 1.764 | 188.5% | With 3.68kW EVSE | 3.732 | 1.803 | 193.5% | Size of Charger ? | 0, 3.68 or 7.36 | 0
50 | 3.737 | 0.031 | 0.8295% |  |  |  | 50 | 1.389 | 0.192 | 13.82% |  |  |  | With 7.36kW (or two 3.68) EVSE | 5.4351 | 3.5061 | 281.8% |  | With 7.36kW (or two 3.68) EVSE | 10.307 | 6.194 | 250.6% | With 7.36kW (or two 3.68) EVSE | 5.6367 | 3.8377 | 313.3% | With 7.36kW (or two 3.68) EVSE | 5.3708 | 3.3778 | 269.5% | With 7.36kW (or two 3.68) EVSE | 5.3351 | 3.4061 | 276.6% | 5KW Heat Pump Installed ? | Yes or No | Yes
75 | 3.713 | 0.044 | 1.185% |  |  |  | 75 | 1.304 | 0.209 | 16.03% |  |  |  | With 3.68kW HP (10kW Heat Output) | 2.5133 | 0.58431 | 130.3% |  | With 3.68kW HP (10kW Heat Output) | 6.523 | 2.41 | 158.6% | With 3.68kW HP (10kW Heat Output) | 3.0303 | 1.2313 | 168.4% | With 3.68kW HP (10kW Heat Output) | 2.7521 | 0.75905 | 138.1% | With 3.68kW HP (10kW Heat Output) | 2.2548 | 0.32581 | 116.9% | Battery Storage ? | Yes or No | No
100 | 3.688 | 0.053 | 1.437% |  |  |  | 100 | 1.276 | 0.092 | 7.21% |  |  |  | With 3.68kW HP + 7.36kW EVSE | 5.697 | 3.768 | 295.3% |  | With 3.68kW HP + 7.36kW EVSE | 12.717 | 8.604 | 309.2% | With 3.68kW HP + 7.36kW EVSE | 6.3886 | 4.5896 | 355.1% | With 3.68kW HP + 7.36kW EVSE | 5.4527 | 3.4597 | 273.6% | With 3.68kW HP + 7.36kW EVSE | 5.3431 | 3.4141 | 277% | PV on Roof ? (Must have battery) | Yes or No | No
[35 empty] | Storage Heating Installed ? | Yes or No | No
[35 empty] | Extreme Outside Temp ? (T < - 5C) | Yes or No | No
[35 empty] | Is there a 60A current limitting device ? | Yes or No | No
ADMD Calc House only | [6 empty] | ADMD Calc 5kW (Heat) HP + House | [6 empty] | ADMD for 50 customers with Battery No PV | ADMD | Addition vs Standard | % |  | ADMD for 1 customers with Battery No PV | ADMD | Addition vs Standard | % | ADMD for 25 customers with Battery No PV | ADMD | Addition vs Standard | % | ADMD for 75 customers with Battery No PV | ADMD | Addition vs Standard | % | ADMD for 100 customers with Battery No PV | ADMD | Addition vs Standard | % |  | ADMD Normal Air Temp | 3.0303
Customers | Mean | St Dev | St Dev % |  |  |  | Customers | Mean | St Dev | St Dev % |  |  |  | House only | 1.93 | 0 | 0% |  | House only | 4.11 | 0 | 0% | House only | 1.8 | 0 | 0% | House only | 1.99 | 0 | 0% | House only | 2.07 | 0 | 0%
1 | 4.113 | 0.769 | 18.7% |  |  |  | 1 | 6.523 | 1.98 | 30.35% |  | 5.728 |  | With 3.68kWH Battery storage | 1.1767 | -0.75331 | 60.97% |  | With 3.68kWH Battery storage | 2.5089 | -1.6011 | 61.04% | With 3.68kWH Battery storage | 1.0974 | -0.70261 | 60.97% | With 3.68kWH Battery storage | 1.2133 | -0.77673 | 60.97% | With 3.68kWH Battery storage | 1.2603 | -0.80974 | 60.88% |  | ADMD Extreme Air Temp | 3.0303
25 | 1.799 | 0.343 | 19.07% |  |  |  | 25 | 3.0303 | 0.673 | 22.21% |  | 2.661 | 2.1526 | With 3.68kW EVSE + 3.68kWH Battery storage | 2.3192 | 0.38922 | 120.2% |  | With 3.68kW EVSE + 3.68kWH Battery storage | 4.3981 | 0.2881 | 107% | With 3.68kW EVSE + 3.68kWH Battery storage | 2.4052 | 0.60523 | 133.6% | With 3.68kW EVSE + 3.68kWH Battery storage | 2.158 | 0.16803 | 108.4% | With 3.68kW EVSE + 3.68kWH Battery storage | 2.2765 | 0.20652 | 110%
50 | 1.929 | 0.358 | 18.56% |  |  |  | 50 | 2.5133 | 0.387 | 15.4% |  | 2.207 | 1.2057 | With 7.36kW EVSE + 3.68kWH Battery storage | 3.3154 | 1.3854 | 171.8% |  | With 7.36kW EVSE + 3.68kWH Battery storage | 6.2873 | 2.1773 | 153% | With 7.36kW EVSE + 3.68kWH Battery storage | 3.4384 | 1.6384 | 191% | With 7.36kW EVSE + 3.68kWH Battery storage | 3.085 | 1.095 | 155% | With 7.36kW EVSE + 3.68kWH Battery storage | 3.2544 | 1.1844 | 157.2% |  | ADMD Current Limiter | 3.0303
75 | 1.993 | 0.311 | 15.6% |  |  |  | 75 | 2.3322 | 0.221 | 9.476% |  | 2.048 | 1.0776 | With 3.68kW HP + 3.68kWH Battery storage | 1.5331 | -0.39688 | 79.44% |  | With 3.68kW HP + 3.68kWH Battery storage | 3.979 | -0.13097 | 96.81% | With 3.68kW HP + 3.68kWH Battery storage | 1.8485 | 0.048498 | 102.7% | With 3.68kW HP + 3.68kWH Battery storage | 1.5808 | -0.40922 | 79.44% | With 3.68kW HP + 3.68kWH Battery storage | 1.3754 | -0.69457 | 66.45%
100 | 2.066 | 0.229 | 11.08% |  |  |  | 100 | 2.2548 | 0.128 | 5.677% |  | 1.98 | 1.0343 | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage | 3.4752 | 1.5452 | 180.1% |  | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage | 7.7574 | 3.6474 | 188.7% | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage | 3.8971 | 2.0971 | 216.5% | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage | 3.132 | 1.142 | 157.4% | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage | 3.2593 | 1.1893 | 157.5%
ADMD Calc 3.68kW EVSE + House | [6 empty] | ADMD Calc 5kW (Heat) HP + House + 7.36 kW EVSE | [6 empty] | ADMD for 50 customers with Battery and PV | ADMD | Addition vs Standard | % |  | ADMD for 1 customers with Battery and PV | ADMD | Addition vs Standard | % | ADMD for 25 customers with Battery and PV | ADMD | Addition vs Standard | % | ADMD for 75 customers with Battery and PV | ADMD | Addition vs Standard | % | ADMD for 100 customers with Battery and PV | ADMD | Addition vs Standard | %
Customers | Mean | St Dev | St Dev % |  |  |  | Customers | Mean | St Dev | St Dev % | 1.18 Factor due to differnce between EV HO and HP HO values from NPG (Negated) |  |  | House only | 1.93 | 0 | 0% |  | House only | 4.11 | 0 | 0% | House only | 1.8 | 0 | 0% | House only | 1.99 | 0 | 0% | House only | 2.07 | 0 | 0%
1 | 7.21 | 0.9 | 12.48% |  |  |  | 1 | 12.717 | 2.7238 | 21.42% |  |  |  | With 3.68kWH Battery storage +3kW PV | 1.1414 | -0.78861 | 59.14% |  | With 3.68kWH Battery storage +3kW PV | 2.4337 | -1.6763 | 59.21% | With 3.68kWH Battery storage +3kW PV | 1.0645 | -0.73553 | 59.14% | With 3.68kWH Battery storage +3kW PV | 0.63112 | -1.3589 | 31.71% | With 3.68kWH Battery storage +3kW PV | 1.2225 | -0.84755 | 61.43%
25 | 3.943 | 0.363 | 9.206% |  |  |  | 25 | 6.3886 | 1.0035 | 15.71% |  |  |  | With 3.68kW EVSE + 3.68kWH Battery storage + 3kW PV | 2.2496 | 0.31964 | 116.6% |  | With 3.68kW EVSE + 3.68kWH Battery storage + 3kW PV | 4.2662 | 0.15616 | 103.8% | With 3.68kW EVSE + 3.68kWH Battery storage + 3kW PV | 2.3331 | 0.53307 | 129.6% | With 3.68kW EVSE + 3.68kWH Battery storage + 3kW PV | 2.4487 | 0.45869 | 123% | With 3.68kW EVSE + 3.68kWH Battery storage + 3kW PV | 2.2082 | 0.13822 | 111%
50 | 3.802 | 0.15 | 3.945% |  |  |  | 50 | 5.697 | 0.551 | 9.672% |  |  |  | With 7.36kW EVSE + 3.68kWH Battery storage + 3kW PV | 3.216 | 1.286 | 166.6% |  | With 7.36kW EVSE + 3.68kWH Battery storage + 3kW PV | 6.0987 | 1.9887 | 148.4% | With 7.36kW EVSE + 3.68kWH Battery storage + 3kW PV | 3.3352 | 1.5352 | 185.3% | With 7.36kW EVSE + 3.68kWH Battery storage + 3kW PV | 3.5005 | 1.5105 | 175.9% | With 7.36kW EVSE + 3.68kWH Battery storage + 3kW PV | 3.1568 | 1.0868 | 158.6%
75 | 3.757 | 0.087 | 2.316% |  |  |  | 75 | 5.4527 | 0.32148 | 5.896% |  |  |  | With 3.68kW HP + 3.68kWH Battery storage + 3kW PV | 1.4871 | -0.44287 | 77.05% | Same as C V33 | With 3.68kW HP + 3.68kWH Battery storage + 3kW PV | 3.8597 | -0.25034 | 93.91% | With 3.68kW HP + 3.68kWH Battery storage + 3kW PV | 1.793 | -0.0069566 | 99.61% | With 3.68kW HP + 3.68kWH Battery storage + 3kW PV | 1.7937 | -0.1963 | 90.14% | With 3.68kW HP + 3.68kWH Battery storage + 3kW PV | 1.3342 | -0.73583 | 67.04%
100 | 3.732 | 0.062 | 1.661% |  |  |  | 100 | 5.3431 | 0.19604 | 3.669% |  |  |  | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage +3kW PV | 3.3709 | 1.4409 | 174.7% |  | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage +3kW PV | 7.5246 | 3.4146 | 183.1% | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage +3kW PV | 3.7802 | 1.9802 | 210% | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage +3kW PV | 3.5539 | 1.5639 | 178.6% | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage +3kW PV | 3.1615 | 1.0915 | 158.9%
ADMD Calc 7.36kW EVSE + House
Customers | Mean | St Dev | St Dev % | [17 empty] | 1 coefficients |  |  |  | 25 coefficients |  |  |  | 75 coefficients |  |  |  | 100 coefficients
1 | 10.307 | 1.2866 | 12.48% | [17 empty] | 3.4275 |  |  |  | 1.4992 |  |  |  | 1.6608 |  |  |  | 1.7217
25 | 5.6367 | 0.51892 | 9.206% | [12 empty] | 50 coefficients |  |  |  | 1.753 | 1.1053 |  |  | 2.1918 | 1.3012 |  |  | 1.8851 | 1.3652 |  |  | 1.8064 | 1.6551
50 | 5.4351 | 0.21443 | 3.945% | [12 empty] | 1.6075 | Differnce in starting ADMD for Batt vs NPG Paper |  |  | 2.506 | 1.5801 |  |  | 3.1332 | 1.8601 |  |  | 2.6948 | 1.9516 |  |  | 2.5823 | 2.3661
75 | 5.3708 | 0.12437 | 2.316% | [11 empty] | 1.971 | 1.5127 | Ratio of EV 3.68 kW to HP kW for Cust |  |  | 1.5859 | 1.9496 |  |  | 1.6844 | 2.1082 |  |  | 1.3809 | 1.9813 |  |  | 1.0914 | 2.3696
100 | 5.3351 | 0.088632 | 1.661% | [11 empty] | 2.8176 | 2.1625 | Ratio of EV 7.36 kW to HP kW for Cust |  |  | 3.0919 |  |  |  | 3.5512 |  |  |  | 2.7359 |  |  |  | 2.5862
[15 empty] | 1.3029 | 2.2667 | Ratio of EV 7.36 kW + HP kW to HPkW for Cust
2.9534
EV |  |  |  | HP | HP + EV |  | 0.84158 | DR Factor EV
3.097 | Diff House to 3.68EV | [6 empty] | DR Factor EV
1.8286 | R 1 to 25 |  |  | 2.1526 | 1.9906 | R 1 to 25
1.0371 | R 25 to 50 |  |  | 1.2057 | 1.1214 | R 25 to 50
1.012 | R 50 to 75 |  |  | 1.0776 | 1.0448 | R 50 to 75
1.0067 | R75 to 100 |  |  | 1.0343 | 1.0205 | R75 to 100
ADMD
-
Note on L15: Haynes, Jack: 3.87 from 5kW HP normal continous

## HPC5PC (hidden)
ADMD Calc 3.68kW EVSE Only | [6 empty] | ADMD Calc 3.68kW Heat Pump Only (obselete)
Customers | Mean | St Dev | St Dev % |  |  |  | Customers | Mean | St Dev | St Dev % |  |  | Increases at 50 customers (No Battery or PV) | ADMD | Addition vs Standard | % | 1.18 Factor due to differnce between EV HO and HP HO values from NPG | Increases at 1 customers (No Battery or PV) | ADMD | Addition vs Standard | % | Increases at 25 customers (No Battery or PV) | ADMD | Addition vs Standard | % | Increases at 75 customers (No Battery or PV) | ADMD | Addition vs Standard | % | Increases at 100 customers (No Battery or PV) | ADMD | Addition vs Standard | % | Variables | Options | Input
1 | 3.587 | 0.549 | 15.31% |  |  |  | 1 | 2.844 | 0.549 | 19.3% |  |  | House only | 1.929 | 0 | 0% |  | House only | 4.113 | 0 | 0% | House only | 1.799 | 0 | 0% | House only | 1.993 | 0 | 0% | House only | 2.066 | 0.137 | 0% | Number of Customers on Feeder ? | 1, 25, 50 or 100 | 25
25 | 3.756 | 0.021 | 0.5591% |  |  |  | 25 | 1.58 | 0.317 | 20.06% |  |  | With 3.68kW EVSE | 3.802 | 1.873 | 197.1% |  | With 3.68kW EVSE | 7.21 | 3.097 | 175.3% | With 3.68kW EVSE | 3.943 | 2.144 | 219.2% | With 3.68kW EVSE | 3.757 | 1.764 | 188.5% | With 3.68kW EVSE | 3.732 | 1.803 | 193.5% | Size of Charger ? | 0, 3.68 or 7.36 | 0
50 | 3.737 | 0.031 | 0.8295% |  |  |  | 50 | 1.389 | 0.192 | 13.82% |  |  | With 7.36kW (or two 3.68) EVSE | 5.4351 | 3.5061 | 281.8% |  | With 7.36kW (or two 3.68) EVSE | 10.307 | 6.194 | 250.6% | With 7.36kW (or two 3.68) EVSE | 5.6367 | 3.8377 | 313.3% | With 7.36kW (or two 3.68) EVSE | 5.3708 | 3.3778 | 269.5% | With 7.36kW (or two 3.68) EVSE | 5.3351 | 3.4061 | 276.6% | Heat Pump Installed ? | Yes or No | Yes
75 | 3.713 | 0.044 | 1.185% |  |  |  | 75 | 1.304 | 0.209 | 16.03% |  |  | With 3.68kW HP (10kW Heat Output) | 5.309 | 3.38 | 275.2% |  | With 3.68kW HP (10kW Heat Output) | 8.8417 | 4.7287 | 215% | With 3.68kW HP (10kW Heat Output) | 6.1112 | 4.3122 | 339.7% | With 3.68kW HP (10kW Heat Output) | 6.3401 | 4.3471 | 318.1% | With 3.68kW HP (10kW Heat Output) | 6.4263 | 4.4973 | 333.1% | Battery Storage ? | Yes or No | No
100 | 3.688 | 0.053 | 1.437% |  |  |  | 100 | 1.276 | 0.092 | 7.21% |  |  | With 3.68kW HP + 7.36kW EVSE | 8.3052 | 6.3762 | 430.5% |  | With 3.68kW HP + 7.36kW EVSE | 13.687 | 9.574 | 332.8% | With 3.68kW HP + 7.36kW EVSE | 8.3576 | 6.5586 | 464.6% | With 3.68kW HP + 7.36kW EVSE | 8.305 | 6.312 | 416.7% | With 3.68kW HP + 7.36kW EVSE | 8.3329 | 6.4039 | 432% | PV on Roof ? (Must have battery) | Yes or No | No
[34 empty] | Storage Heating Installed ? | Yes or No | No
[34 empty] | Extreme Outside Temp ? (T < - 5C) | Yes or No | Yes
[34 empty] | Is there a 60A current limitting device ? | Yes or No | No
ADMD Calc House only | [6 empty] | ADMD Calc 5kW (Heat) HP + House | [5 empty] | ADMD for 50 customers with Battery No PV | ADMD | Addition vs Standard | % |  | ADMD for 1 customers with Battery No PV | ADMD | Addition vs Standard | % | ADMD for 25 customers with Battery No PV | ADMD | Addition vs Standard | % | ADMD for 75 customers with Battery No PV | ADMD | Addition vs Standard | % | ADMD for 100 customers with Battery No PV | ADMD | Addition vs Standard | % |  | ADMD Normal Air Temp | 6.1112
Customers | Mean | St Dev | St Dev % |  |  |  | Customers | Mean | St Dev | St Dev % |  |  | House only | 1.93 | 0 | 0% |  | House only | 4.11 | 0 | 0% | House only | 1.8 | 0 | 0% | House only | 1.99 | 0 | 0% | House only | 2.07 | 0 | 0%
1 | 4.113 | 0.769 | 18.7% |  |  |  | 1 | 7.493 | 1.98 | 26.42% | 5.728 |  | With 3.68kWH Battery storage | 1.1767 | -0.75331 | 60.97% |  | With 3.68kWH Battery storage | 2.5089 | -1.6011 | 61.04% | With 3.68kWH Battery storage | 1.0974 | -0.70261 | 60.97% | With 3.68kWH Battery storage | 1.2133 | -0.77673 | 60.97% | With 3.68kWH Battery storage | 1.2603 | -0.80974 | 60.88% |  | ADMD Extreme Air Temp | 9.0552
25 | 1.799 | 0.343 | 19.07% |  |  |  | 25 | 5.179 | 0.673 | 12.99% | 2.661 | 2.1526 | With 3.68kW EVSE + 3.68kWH Battery storage | 2.3192 | 0.38922 | 120.2% |  | With 3.68kW EVSE + 3.68kWH Battery storage | 4.3981 | 0.2881 | 107% | With 3.68kW EVSE + 3.68kWH Battery storage | 2.4052 | 0.60523 | 133.6% | With 3.68kW EVSE + 3.68kWH Battery storage | 2.158 | 0.16803 | 108.4% | With 3.68kW EVSE + 3.68kWH Battery storage | 2.2765 | 0.20652 | 110%
50 | 1.929 | 0.358 | 18.56% |  |  |  | 50 | 5.309 | 0.387 | 7.29% | 2.207 | 1.2057 | With 7.36kW EVSE + 3.68kWH Battery storage | 3.3154 | 1.3854 | 171.8% |  | With 7.36kW EVSE + 3.68kWH Battery storage | 6.2873 | 2.1773 | 153% | With 7.36kW EVSE + 3.68kWH Battery storage | 3.4384 | 1.6384 | 191% | With 7.36kW EVSE + 3.68kWH Battery storage | 3.085 | 1.095 | 155% | With 7.36kW EVSE + 3.68kWH Battery storage | 3.2544 | 1.1844 | 157.2% |  | ADMD Current Limiter | 9.0552
75 | 1.993 | 0.311 | 15.6% |  |  |  | 75 | 5.373 | 0.221 | 4.113% | 2.048 | 1.0776 | With 3.68kW HP + 3.68kWH Battery storage | 1.5331 | -0.39688 | 79.44% |  | With 3.68kW HP + 3.68kWH Battery storage | 3.979 | -0.13097 | 96.81% | With 3.68kW HP + 3.68kWH Battery storage | 1.8485 | 0.048498 | 102.7% | With 3.68kW HP + 3.68kWH Battery storage | 1.5808 | -0.40922 | 79.44% | With 3.68kW HP + 3.68kWH Battery storage | 1.3754 | -0.69457 | 66.45%
100 | 2.066 | 0.229 | 11.08% |  |  |  | 100 | 5.446 | 0.128 | 2.35% | 1.98 | 1.0343 | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage | 3.4752 | 1.5452 | 180.1% |  | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage | 7.7574 | 3.6474 | 188.7% | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage | 3.8971 | 2.0971 | 216.5% | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage | 3.132 | 1.142 | 157.4% | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage | 3.2593 | 1.1893 | 157.5%
ADMD Calc 3.68kW EVSE + House | [6 empty] | ADMD Calc 5kW (Heat) HP + House + 7.36 kW EVSE | [5 empty] | ADMD for 50 customers with Battery and PV | ADMD | Addition vs Standard | % |  | ADMD for 1 customers with Battery and PV | ADMD | Addition vs Standard | % | ADMD for 25 customers with Battery and PV | ADMD | Addition vs Standard | % | ADMD for 75 customers with Battery and PV | ADMD | Addition vs Standard | % | ADMD for 100 customers with Battery and PV | ADMD | Addition vs Standard | %
Customers | Mean | St Dev | St Dev % |  |  |  | Customers | Mean | St Dev | St Dev % |  |  | House only | 1.93 | 0 | 0% |  | House only | 4.11 | 0 | 0% | House only | 1.8 | 0 | 0% | House only | 1.99 | 0 | 0% | House only | 2.07 | 0 | 0%
1 | 7.21 | 0.9 | 12.48% |  |  |  | 1 | 13.687 | 2.6626 | 19.45% |  |  | With 3.68kWH Battery storage +3kW PV | 1.1414 | -0.78861 | 59.14% |  | With 3.68kWH Battery storage +3kW PV | 2.4337 | -1.6763 | 59.21% | With 3.68kWH Battery storage +3kW PV | 1.0645 | -0.73553 | 59.14% | With 3.68kWH Battery storage +3kW PV | 0.63112 | -1.3589 | 31.71% | With 3.68kWH Battery storage +3kW PV | 1.2225 | -0.84755 | 61.43%
25 | 3.943 | 0.363 | 9.206% |  |  |  | 25 | 8.3576 | 0.92773 | 11.1% |  |  | With 3.68kW EVSE + 3.68kWH Battery storage + 3kW PV | 2.2496 | 0.31964 | 116.6% |  | With 3.68kW EVSE + 3.68kWH Battery storage + 3kW PV | 4.2662 | 0.15616 | 103.8% | With 3.68kW EVSE + 3.68kWH Battery storage + 3kW PV | 2.3331 | 0.53307 | 129.6% | With 3.68kW EVSE + 3.68kWH Battery storage + 3kW PV | 2.4487 | 0.45869 | 123% | With 3.68kW EVSE + 3.68kWH Battery storage + 3kW PV | 2.2082 | 0.13822 | 111%
50 | 3.802 | 0.15 | 3.945% |  |  |  | 50 | 8.3052 | 0.46654 | 5.617% |  |  | With 7.36kW EVSE + 3.68kWH Battery storage + 3kW PV | 3.216 | 1.286 | 166.6% |  | With 7.36kW EVSE + 3.68kWH Battery storage + 3kW PV | 6.0987 | 1.9887 | 148.4% | With 7.36kW EVSE + 3.68kWH Battery storage + 3kW PV | 3.3352 | 1.5352 | 185.3% | With 7.36kW EVSE + 3.68kWH Battery storage + 3kW PV | 3.5005 | 1.5105 | 175.9% | With 7.36kW EVSE + 3.68kWH Battery storage + 3kW PV | 3.1568 | 1.0868 | 158.6%
75 | 3.757 | 0.087 | 2.316% |  |  |  | 75 | 8.305 | 0.26696 | 3.214% |  |  | With 3.68kW HP + 3.68kWH Battery storage + 3kW PV | 1.4871 | -0.44287 | 77.05% | Same as C V33 | With 3.68kW HP + 3.68kWH Battery storage + 3kW PV | 3.8597 | -0.25034 | 93.91% | With 3.68kW HP + 3.68kWH Battery storage + 3kW PV | 1.793 | -0.0069566 | 99.61% | With 3.68kW HP + 3.68kWH Battery storage + 3kW PV | 1.7937 | -0.1963 | 90.14% | With 3.68kW HP + 3.68kWH Battery storage + 3kW PV | 1.3342 | -0.73583 | 67.04%
100 | 3.732 | 0.062 | 1.661% |  |  |  | 100 | 8.3329 | 0.16714 | 2.006% |  |  | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage +3kW PV | 3.3709 | 1.4409 | 174.7% |  | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage +3kW PV | 7.5246 | 3.4146 | 183.1% | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage +3kW PV | 3.7802 | 1.9802 | 210% | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage +3kW PV | 3.5539 | 1.5639 | 178.6% | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage +3kW PV | 3.1615 | 1.0915 | 158.9%
ADMD Calc 7.36kW EVSE + House
Customers | Mean | St Dev | St Dev % | [16 empty] | 1 coefficients |  |  |  | 25 coefficients |  |  |  | 75 coefficients |  |  |  | 100 coefficients
1 | 10.307 | 1.2866 | 12.48% | [16 empty] | 3.4275 |  |  |  | 1.4992 |  |  |  | 1.6608 |  |  |  | 1.7217
25 | 5.6367 | 0.51892 | 9.206% | [11 empty] | 50 coefficients |  |  |  | 1.753 | 0.81545 |  |  | 2.1918 | 0.64521 |  |  | 1.8851 | 0.59257 |  |  | 1.8064 | 0.58074
50 | 5.4351 | 0.21443 | 3.945% | [11 empty] | 1.6075 | Differnce in starting ADMD for Batt vs NPG Paper |  |  | 2.506 | 1.1657 |  |  | 3.1332 | 0.92235 |  |  | 2.6948 | 0.84711 |  |  | 2.5823 | 0.83019
75 | 5.3708 | 0.12437 | 2.316% | [10 empty] | 1.971 | 0.71614 | Ratio of EV 3.68 kW to HP kW for Cust |  |  | 2.1497 | 1.548 |  |  | 3.397 | 1.3676 |  |  | 3.1812 | 1.3099 |  |  | 3.1105 | 1.2967
100 | 5.3351 | 0.088632 | 1.661% | [10 empty] | 2.8176 | 1.0238 | Ratio of EV 7.36 kW to HP kW for Cust |  |  | 3.3277 |  |  |  | 4.6457 |  |  |  | 4.1671 |  |  |  | 4.0333
[14 empty] | 2.7522 | 1.5644 | Ratio of EV 7.36 kW + HP kW to HPkW for Cust
4.3055
EV |  |  |  | HP | HP + EV |  | 0.84158 | DR Factor EV
3.097 | Diff House to 3.68EV | [6 empty] | DR Factor EV
1.8286 | R 1 to 25 |  |  | 1.4468 | 1.6377 | R 1 to 25
1.0371 | R 25 to 50 |  |  | 0.97551 | 1.0063 | R 25 to 50
1.012 | R 50 to 75 |  |  | 0.98809 | 1 | R 50 to 75
1.0067 | R75 to 100 |  |  | 0.9866 | 0.99665 | R75 to 100
ADMD
-
Note on L15: Haynes, Jack: 3.87 from 5kW HP normal continous

## HPC8N (hidden)
ADMD Calc 3.68kW EVSE Only | [6 empty] | ADMD Calc 3.68kW Heat Pump Only (obselete)
Customers | Mean | St Dev | St Dev % |  |  |  | Customers | Mean | St Dev | St Dev % |  |  |  | Increases at 50 customers (No Battery or PV) | ADMD | Addition vs Standard | % | 1.18 Factor due to differnce between EV HO and HP HO values from NPG | Increases at 1 customers (No Battery or PV) | ADMD | Addition vs Standard | % | Increases at 25 customers (No Battery or PV) | ADMD | Addition vs Standard | % | Increases at 75 customers (No Battery or PV) | ADMD | Addition vs Standard | % | Increases at 100 customers (No Battery or PV) | ADMD | Addition vs Standard | % | Variables | Options | Input
1 | 3.587 | 0.549 | 15.31% |  |  |  | 1 | 2.844 | 0.549 | 19.3% |  |  |  | House only | 1.929 | 0 | 0% |  | House only | 4.113 | 0 | 0% | House only | 1.799 | 0 | 0% | House only | 1.993 | 0 | 0% | House only | 2.066 | 0.137 | 0% | Number of Customers on Feeder ? | 1, 25, 50 or 100 | 25
25 | 3.756 | 0.021 | 0.5591% |  |  |  | 25 | 1.58 | 0.317 | 20.06% |  |  |  | With 3.68kW EVSE | 3.802 | 1.873 | 197.1% |  | With 3.68kW EVSE | 7.21 | 3.097 | 175.3% | With 3.68kW EVSE | 3.943 | 2.144 | 219.2% | With 3.68kW EVSE | 3.757 | 1.764 | 188.5% | With 3.68kW EVSE | 3.732 | 1.803 | 193.5% | Size of Charger ? | 0, 3.68 or 7.36 | 0
50 | 3.737 | 0.031 | 0.8295% |  |  |  | 50 | 1.389 | 0.192 | 13.82% |  |  |  | With 7.36kW (or two 3.68) EVSE | 5.4351 | 3.5061 | 281.8% |  | With 7.36kW (or two 3.68) EVSE | 10.307 | 6.194 | 250.6% | With 7.36kW (or two 3.68) EVSE | 5.6367 | 3.8377 | 313.3% | With 7.36kW (or two 3.68) EVSE | 5.3708 | 3.3778 | 269.5% | With 7.36kW (or two 3.68) EVSE | 5.3351 | 3.4061 | 276.6% | Heat Pump Installed ? | Yes or No | Yes
75 | 3.713 | 0.044 | 1.185% |  |  |  | 75 | 1.304 | 0.209 | 16.03% |  |  |  | With 3.68kW HP (10kW Heat Output) | 3.3879 | 1.4589 | 175.6% |  | With 3.68kW HP (10kW Heat Output) | 8.793 | 4.68 | 213.8% | With 3.68kW HP (10kW Heat Output) | 4.0849 | 2.2859 | 227.1% | With 3.68kW HP (10kW Heat Output) | 3.1439 | 1.1509 | 157.7% | With 3.68kW HP (10kW Heat Output) | 3.0395 | 1.1105 | 157.6% | Battery Storage ? | Yes or No | No
100 | 3.688 | 0.053 | 1.437% |  |  |  | 100 | 1.276 | 0.092 | 7.21% |  |  |  | With 3.68kW HP + 7.36kW EVSE | 7.2134 | 5.2844 | 373.9% |  | With 3.68kW HP + 7.36kW EVSE | 16.1019 | 11.9889 | 391.5% | With 3.68kW HP + 7.36kW EVSE | 8.0891 | 6.2901 | 449.6% | With 3.68kW HP + 7.36kW EVSE | 6.9041 | 4.9111 | 346.4% | With 3.68kW HP + 7.36kW EVSE | 6.7652 | 4.8362 | 350.7% | PV on Roof ? (Must have battery) | Yes or No | No
[35 empty] | Storage Heating Installed ? | Yes or No | No
[35 empty] | Extreme Outside Temp ? (T < - 5C) | Yes or No | Yes
[35 empty] | Is there a 60A current limitting device ? | Yes or No | No
ADMD Calc House only | [6 empty] | ADMD Calc 5kW (Heat) HP + House | [6 empty] | ADMD for 50 customers with Battery No PV | ADMD | Addition vs Standard | % |  | ADMD for 1 customers with Battery No PV | ADMD | Addition vs Standard | % | ADMD for 25 customers with Battery No PV | ADMD | Addition vs Standard | % | ADMD for 75 customers with Battery No PV | ADMD | Addition vs Standard | % | ADMD for 100 customers with Battery No PV | ADMD | Addition vs Standard | % |  | ADMD Normal Air Temp | 4.0849
Customers | Mean | St Dev | St Dev % |  |  |  | Customers | Mean | St Dev | St Dev % |  |  |  | House only | 1.93 | 0 | 0% |  | House only | 4.11 | 0 | 0% | House only | 1.8 | 0 | 0% | House only | 1.99 | 0 | 0% | House only | 2.07 | 0 | 0%
1 | 4.113 | 0.769 | 18.7% |  |  |  | 1 | 8.793 | 1.98 | 22.52% |  | 5.728 |  | With 3.68kWH Battery storage | 1.1767 | -0.75331 | 60.97% |  | With 3.68kWH Battery storage | 2.5089 | -1.6011 | 61.04% | With 3.68kWH Battery storage | 1.0974 | -0.70261 | 60.97% | With 3.68kWH Battery storage | 1.2157 | -0.77427 | 61.09% | With 3.68kWH Battery storage | 1.2603 | -0.80974 | 60.88% |  | ADMD Extreme Air Temp | 7.0289
25 | 1.799 | 0.343 | 19.07% |  |  |  | 25 | 4.0849 | 0.673 | 16.48% |  | 2.661 | 2.1526 | With 3.68kW EVSE + 3.68kWH Battery storage | 2.3192 | 0.38922 | 120.2% |  | With 3.68kW EVSE + 3.68kWH Battery storage | 4.3981 | 0.2881 | 107% | With 3.68kW EVSE + 3.68kWH Battery storage | 2.4052 | 0.60523 | 133.6% | With 3.68kW EVSE + 3.68kWH Battery storage | 2.2918 | 0.30177 | 115.2% | With 3.68kW EVSE + 3.68kWH Battery storage | 2.2765 | 0.20652 | 110%
50 | 1.929 | 0.358 | 18.56% |  |  |  | 50 | 3.3879 | 0.387 | 11.42% |  | 2.207 | 1.2057 | With 7.36kW EVSE + 3.68kWH Battery storage | 3.3154 | 1.3854 | 171.8% |  | With 7.36kW EVSE + 3.68kWH Battery storage | 6.2873 | 2.1773 | 153% | With 7.36kW EVSE + 3.68kWH Battery storage | 3.4384 | 1.6384 | 191% | With 7.36kW EVSE + 3.68kWH Battery storage | 3.2762 | 1.2862 | 164.6% | With 7.36kW EVSE + 3.68kWH Battery storage | 3.2544 | 1.1844 | 157.2% |  | ADMD Current Limiter | 7.0289
75 | 1.993 | 0.311 | 15.6% |  |  |  | 75 | 3.1439 | 0.221 | 7.03% |  | 2.048 | 1.0776 | With 3.68kW HP + 3.68kWH Battery storage | 2.0666 | 0.13665 | 107.1% |  | With 3.68kW HP + 3.68kWH Battery storage | 5.3637 | 1.2537 | 130.5% | With 3.68kW HP + 3.68kWH Battery storage | 2.4918 | 0.69177 | 138.4% | With 3.68kW HP + 3.68kWH Battery storage | 1.9178 | -0.072242 | 96.37% | With 3.68kW HP + 3.68kWH Battery storage | 1.8541 | -0.21592 | 89.57%
100 | 2.066 | 0.229 | 11.08% |  |  |  | 100 | 3.0395 | 0.128 | 4.211% |  | 1.98 | 1.0343 | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage | 4.4002 | 2.4702 | 228% |  | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage | 9.8222 | 5.7122 | 239% | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage | 4.9344 | 3.1344 | 274.1% | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage | 4.2115 | 2.2215 | 211.6% | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage | 4.1268 | 2.0568 | 199.4%
ADMD Calc 3.68kW EVSE + House | [6 empty] | ADMD Calc 5kW (Heat) HP + House + 7.36 kW EVSE | [6 empty] | ADMD for 50 customers with Battery and PV | ADMD | Addition vs Standard | % |  | ADMD for 1 customers with Battery and PV | ADMD | Addition vs Standard | % | ADMD for 25 customers with Battery and PV | ADMD | Addition vs Standard | % | ADMD for 75 customers with Battery and PV | ADMD | Addition vs Standard | % | ADMD for 100 customers with Battery and PV | ADMD | Addition vs Standard | %
Customers | Mean | St Dev | St Dev % |  |  |  | Customers | Mean | St Dev | St Dev % | 1.18 Factor due to differnce between EV HO and HP HO values from NPG |  |  | House only | 1.93 | 0 | 0% |  | House only | 4.11 | 0 | 0% | House only | 1.8 | 0 | 0% | House only | 1.99 | 0 | 0% | House only | 2.07 | 0 | 0%
1 | 7.21 | 0.9 | 12.48% |  |  |  | 1 | 16.1019 | 2.8179 | 17.5% |  |  |  | With 3.68kWH Battery storage +3kW PV | 1.1414 | -0.78861 | 59.14% |  | With 3.68kWH Battery storage +3kW PV | 2.4337 | -1.6763 | 59.21% | With 3.68kWH Battery storage +3kW PV | 1.0645 | -0.73553 | 59.14% | With 3.68kWH Battery storage +3kW PV | 1.1793 | -0.81074 | 59.26% | With 3.68kWH Battery storage +3kW PV | 1.2225 | -0.84755 | 61.43%
25 | 3.943 | 0.363 | 9.206% |  |  |  | 25 | 8.0891 | 1.0387 | 12.84% |  |  |  | With 3.68kW EVSE + 3.68kWH Battery storage + 3kW PV | 2.2496 | 0.31964 | 116.6% |  | With 3.68kW EVSE + 3.68kWH Battery storage + 3kW PV | 4.2662 | 0.15616 | 103.8% | With 3.68kW EVSE + 3.68kWH Battery storage + 3kW PV | 2.3331 | 0.53307 | 129.6% | With 3.68kW EVSE + 3.68kWH Battery storage + 3kW PV | 2.223 | 0.23302 | 111.7% | With 3.68kW EVSE + 3.68kWH Battery storage + 3kW PV | 2.2082 | 0.13822 | 111%
50 | 3.802 | 0.15 | 3.945% |  |  |  | 50 | 7.2134 | 0.55428 | 7.684% |  |  |  | With 7.36kW EVSE + 3.68kWH Battery storage + 3kW PV | 3.216 | 1.286 | 166.6% |  | With 7.36kW EVSE + 3.68kWH Battery storage + 3kW PV | 6.0987 | 1.9887 | 148.4% | With 7.36kW EVSE + 3.68kWH Battery storage + 3kW PV | 3.3352 | 1.5352 | 185.3% | With 7.36kW EVSE + 3.68kWH Battery storage + 3kW PV | 3.1779 | 1.1879 | 159.7% | With 7.36kW EVSE + 3.68kWH Battery storage + 3kW PV | 3.1568 | 1.0868 | 158.6%
75 | 3.757 | 0.087 | 2.316% |  |  |  | 75 | 6.9041 | 0.3226 | 4.673% |  |  |  | With 3.68kW HP + 3.68kWH Battery storage + 3kW PV | 2.0046 | 0.074647 | 103.9% | Same as C V33 | With 3.68kW HP + 3.68kWH Battery storage + 3kW PV | 5.2028 | 1.0928 | 126.6% | With 3.68kW HP + 3.68kWH Battery storage + 3kW PV | 2.417 | 0.61702 | 134.3% | With 3.68kW HP + 3.68kWH Battery storage + 3kW PV | 1.8602 | -0.12977 | 93.48% | With 3.68kW HP + 3.68kWH Battery storage + 3kW PV | 1.7985 | -0.27154 | 90.37%
100 | 3.732 | 0.062 | 1.661% |  |  |  | 100 | 6.7652 | 0.19865 | 2.936% |  |  |  | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage +3kW PV | 4.2682 | 2.3382 | 221.1% |  | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage +3kW PV | 9.5275 | 5.4175 | 231.8% | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage +3kW PV | 4.7863 | 2.9863 | 265.9% | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage +3kW PV | 4.0851 | 2.0951 | 205.3% | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage +3kW PV | 4.003 | 1.933 | 201.2%
ADMD Calc 7.36kW EVSE + House
Customers | Mean | St Dev | St Dev % | [17 empty] | 1 coefficients |  |  |  | 25 coefficients |  |  |  | 75 coefficients |  |  |  | 100 coefficients
1 | 10.307 | 1.2866 | 12.48% | [17 empty] | 3.4275 |  |  |  | 1.4992 |  |  |  | 1.6608 |  |  |  | 1.7217
25 | 5.6367 | 0.51892 | 9.206% | [12 empty] | 50 coefficients |  |  |  | 1.753 | 0.81997 |  |  | 2.1918 | 0.96527 |  |  | 1.8851 | 1.195 |  |  | 1.8064 | 1.2278
50 | 5.4351 | 0.21443 | 3.945% | [12 empty] | 1.6075 | Differnce in starting ADMD for Batt vs NPG Paper |  |  | 2.506 | 1.1722 |  |  | 3.1332 | 1.3799 |  |  | 2.6948 | 1.7083 |  |  | 2.5823 | 1.7553
75 | 5.3708 | 0.12437 | 2.316% | [11 empty] | 1.971 | 1.1222 | Ratio of EV 3.68 kW to HP kW for Cust |  |  | 2.1379 | 1.8312 |  |  | 2.2706 | 1.9803 |  |  | 1.5775 | 2.196 |  |  | 1.4712 | 2.2258
100 | 5.3351 | 0.088632 | 1.661% | [11 empty] | 2.8176 | 1.6043 | Ratio of EV 7.36 kW to HP kW for Cust |  |  | 3.9149 |  |  |  | 4.4965 |  |  |  | 3.4642 |  |  |  | 3.2746
[15 empty] | 1.7563 | 2.1291 | Ratio of EV 7.36 kW + HP kW to HPkW for Cust
3.7395
EV |  |  |  | HP | HP + EV |  | 0.84158 | DR Factor EV
3.097 | Diff House to 3.68EV | [6 empty] | DR Factor EV
1.8286 | R 1 to 25 |  |  | 2.1526 | 1.9906 | R 1 to 25
1.0371 | R 25 to 50 |  |  | 1.2057 | 1.1214 | R 25 to 50
1.012 | R 50 to 75 |  |  | 1.0776 | 1.0448 | R 50 to 75
1.0067 | R75 to 100 |  |  | 1.0343 | 1.0205 | R75 to 100
ADMD
-
Note on L15: Haynes, Jack: 3.87 from 5kW HP normal continous

## HPC8PC (hidden)
ADMD Calc 3.68kW EVSE Only | [6 empty] | ADMD Calc 3.68kW Heat Pump Only (obselete)
Customers | Mean | St Dev | St Dev % |  |  |  | Customers | Mean | St Dev | St Dev % |  |  |  | Increases at 50 customers (No Battery or PV) | ADMD | Addition vs Standard | % | 1.18 Factor due to differnce between EV HO and HP HO values from NPG | Increases at 1 customers (No Battery or PV) | ADMD | Addition vs Standard | % | Increases at 25 customers (No Battery or PV) | ADMD | Addition vs Standard | % | Increases at 75 customers (No Battery or PV) | ADMD | Addition vs Standard | % | Increases at 100 customers (No Battery or PV) | ADMD | Addition vs Standard | % | Variables | Options | Input
1 | 3.587 | 0.549 | 15.31% |  |  |  | 1 | 2.844 | 0.549 | 19.3% |  |  |  | House only | 1.929 | 0 | 0% |  | House only | 4.113 | 0 | 0% | House only | 1.799 | 0 | 0% | House only | 1.993 | 0 | 0% | House only | 2.066 | 0.137 | 0% | Number of Customers on Feeder ? | 1, 25, 50 or 100 | 25
25 | 3.756 | 0.021 | 0.5591% |  |  |  | 25 | 1.58 | 0.317 | 20.06% |  |  |  | With 3.68kW EVSE | 3.802 | 1.873 | 197.1% |  | With 3.68kW EVSE | 7.21 | 3.097 | 175.3% | With 3.68kW EVSE | 3.943 | 2.144 | 219.2% | With 3.68kW EVSE | 3.757 | 1.764 | 188.5% | With 3.68kW EVSE | 3.732 | 1.803 | 193.5% | Size of Charger ? | 0, 3.68 or 7.36 | 0
50 | 3.737 | 0.031 | 0.8295% |  |  |  | 50 | 1.389 | 0.192 | 13.82% |  |  |  | With 7.36kW (or two 3.68) EVSE | 5.4351 | 3.5061 | 281.8% |  | With 7.36kW (or two 3.68) EVSE | 10.307 | 6.194 | 250.6% | With 7.36kW (or two 3.68) EVSE | 5.6367 | 3.8377 | 313.3% | With 7.36kW (or two 3.68) EVSE | 5.3708 | 3.3778 | 269.5% | With 7.36kW (or two 3.68) EVSE | 5.3351 | 3.4061 | 276.6% | Heat Pump Installed ? | Yes or No | Yes
75 | 3.713 | 0.044 | 1.185% |  |  |  | 75 | 1.304 | 0.209 | 16.03% |  |  |  | With 3.68kW HP (10kW Heat Output) | 8.479 | 6.55 | 439.6% |  | With 3.68kW HP (10kW Heat Output) | 10.663 | 6.55 | 259.3% | With 3.68kW HP (10kW Heat Output) | 8.349 | 6.55 | 464.1% | With 3.68kW HP (10kW Heat Output) | 8.543 | 6.55 | 428.7% | With 3.68kW HP (10kW Heat Output) | 8.616 | 6.687 | 446.7% | Battery Storage ? | Yes or No | No
100 | 3.688 | 0.053 | 1.437% |  |  |  | 100 | 1.276 | 0.092 | 7.21% |  |  |  | With 3.68kW HP + 7.36kW EVSE | 11.4489 | 9.5199 | 593.5% |  | With 3.68kW HP + 7.36kW EVSE | 17.9719 | 13.8589 | 437% | With 3.68kW HP + 7.36kW EVSE | 11.5734 | 9.7744 | 643.3% | With 3.68kW HP + 7.36kW EVSE | 11.4233 | 9.4303 | 573.2% | With 3.68kW HP + 7.36kW EVSE | 11.4334 | 9.5044 | 592.7% | PV on Roof ? (Must have battery) | Yes or No | No
[35 empty] | Storage Heating Installed ? | Yes or No | No
[35 empty] | Extreme Outside Temp ? (T < - 5C) | Yes or No | Yes
[35 empty] | Is there a 60A current limitting device ? | Yes or No | No
ADMD Calc House only | [6 empty] | ADMD Calc 8kW (Heat) HP + House | [6 empty] | ADMD for 50 customers with Battery No PV | ADMD | Addition vs Standard | % |  | ADMD for 1 customers with Battery No PV | ADMD | Addition vs Standard | % | ADMD for 25 customers with Battery No PV | ADMD | Addition vs Standard | % | ADMD for 75 customers with Battery No PV | ADMD | Addition vs Standard | % | ADMD for 100 customers with Battery No PV | ADMD | Addition vs Standard | % |  | ADMD Normal Air Temp | 8.349
Customers | Mean | St Dev | St Dev % |  |  |  | Customers | Mean | St Dev | St Dev % |  |  |  | House only | 1.93 | 0 | 0% |  | House only | 4.11 | 0 | 0% | House only | 1.8 | 0 | 0% | House only | 1.99 | 0 | 0% | House only | 2.07 | 0 | 0%
1 | 4.113 | 0.769 | 18.7% |  |  |  | 1 | 10.663 | 1.98 | 18.57% |  | 5.728 |  | With 3.68kWH Battery storage | 1.1767 | -0.75331 | 60.97% |  | With 3.68kWH Battery storage | 2.5089 | -1.6011 | 61.04% | With 3.68kWH Battery storage | 1.0974 | -0.70261 | 60.97% | With 3.68kWH Battery storage | 1.2157 | -0.77427 | 61.09% | With 3.68kWH Battery storage | 1.2603 | -0.80974 | 60.88% |  | ADMD Extreme Air Temp | 11.293
25 | 1.799 | 0.343 | 19.07% |  |  |  | 25 | 8.349 | 0.673 | 8.061% |  | 2.661 | 2.1526 | With 3.68kW EVSE + 3.68kWH Battery storage | 2.3192 | 0.38922 | 120.2% |  | With 3.68kW EVSE + 3.68kWH Battery storage | 4.3981 | 0.2881 | 107% | With 3.68kW EVSE + 3.68kWH Battery storage | 2.4052 | 0.60523 | 133.6% | With 3.68kW EVSE + 3.68kWH Battery storage | 2.2918 | 0.30177 | 115.2% | With 3.68kW EVSE + 3.68kWH Battery storage | 2.2765 | 0.20652 | 110%
50 | 1.929 | 0.358 | 18.56% |  |  |  | 50 | 8.479 | 0.387 | 4.564% |  | 2.207 | 1.2057 | With 7.36kW EVSE + 3.68kWH Battery storage | 3.3154 | 1.3854 | 171.8% |  | With 7.36kW EVSE + 3.68kWH Battery storage | 6.2873 | 2.1773 | 153% | With 7.36kW EVSE + 3.68kWH Battery storage | 3.4384 | 1.6384 | 191% | With 7.36kW EVSE + 3.68kWH Battery storage | 3.2762 | 1.2862 | 164.6% | With 7.36kW EVSE + 3.68kWH Battery storage | 3.2544 | 1.1844 | 157.2% |  | ADMD Current Limiter | 11.293
75 | 1.993 | 0.311 | 15.6% |  |  |  | 75 | 8.543 | 0.221 | 2.587% |  | 2.048 | 1.0776 | With 3.68kW HP + 3.68kWH Battery storage | 2.0666 | 0.13665 | 107.1% |  | With 3.68kW HP + 3.68kWH Battery storage | 5.3637 | 1.2537 | 130.5% | With 3.68kW HP + 3.68kWH Battery storage | 2.4918 | 0.69177 | 138.4% | With 3.68kW HP + 3.68kWH Battery storage | 1.9178 | -0.072242 | 96.37% | With 3.68kW HP + 3.68kWH Battery storage | 1.8541 | -0.21592 | 89.57%
100 | 2.066 | 0.229 | 11.08% |  |  |  | 100 | 8.616 | 0.128 | 1.486% |  | 1.98 | 1.0343 | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage | 4.4002 | 2.4702 | 228% |  | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage | 9.8222 | 5.7122 | 239% | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage | 4.9344 | 3.1344 | 274.1% | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage | 4.2115 | 2.2215 | 211.6% | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage | 4.1268 | 2.0568 | 199.4%
ADMD Calc 3.68kW EVSE + House | [6 empty] | ADMD Calc 8kW (Heat) HP + House + 7.36 kW EVSE | [6 empty] | ADMD for 50 customers with Battery and PV | ADMD | Addition vs Standard | % |  | ADMD for 1 customers with Battery and PV | ADMD | Addition vs Standard | % | ADMD for 25 customers with Battery and PV | ADMD | Addition vs Standard | % | ADMD for 75 customers with Battery and PV | ADMD | Addition vs Standard | % | ADMD for 100 customers with Battery and PV | ADMD | Addition vs Standard | %
Customers | Mean | St Dev | St Dev % |  |  |  | Customers | Mean | St Dev | St Dev % | 1.18 Factor due to differnce between EV HO and HP HO values from NPG |  |  | House only | 1.93 | 0 | 0% |  | House only | 1.93 | 0 | 0% | House only | 1.93 | 0 | 0% | House only | 1.93 | 0 | 0% | House only | 1.93 | 0 | 0%
1 | 7.21 | 0.9 | 12.48% |  |  |  | 1 | 17.9719 | 2.7903 | 15.53% |  |  |  | With 3.68kWH Battery storage +3kW PV | 1.1414 | -0.78861 | 59.14% |  | With 3.68kWH Battery storage +3kW PV | 2.4337 | -1.6763 | 59.21% | With 3.68kWH Battery storage +3kW PV | 1.0645 | -0.73553 | 59.14% | With 3.68kWH Battery storage +3kW PV | 1.1793 | -0.81074 | 59.26% | With 3.68kWH Battery storage +3kW PV | 1.2225 | -0.84755 | 61.43%
25 | 3.943 | 0.363 | 9.206% |  |  |  | 25 | 11.5734 | 0.9992 | 8.634% |  |  |  | With 3.68kW EVSE + 3.68kWH Battery storage + 3kW PV | 2.2496 | 0.31964 | 116.6% |  | With 3.68kW EVSE + 3.68kWH Battery storage + 3kW PV | 4.2662 | 0.15616 | 103.8% | With 3.68kW EVSE + 3.68kWH Battery storage + 3kW PV | 2.3331 | 0.53307 | 129.6% | With 3.68kW EVSE + 3.68kWH Battery storage + 3kW PV | 2.223 | 0.23302 | 111.7% | With 3.68kW EVSE + 3.68kWH Battery storage + 3kW PV | 2.2082 | 0.13822 | 111%
50 | 3.802 | 0.15 | 3.945% |  |  |  | 50 | 11.4489 | 0.48712 | 4.255% |  |  |  | With 7.36kW EVSE + 3.68kWH Battery storage + 3kW PV | 3.216 | 1.286 | 166.6% |  | With 7.36kW EVSE + 3.68kWH Battery storage + 3kW PV | 6.0987 | 1.9887 | 148.4% | With 7.36kW EVSE + 3.68kWH Battery storage + 3kW PV | 3.3352 | 1.5352 | 185.3% | With 7.36kW EVSE + 3.68kWH Battery storage + 3kW PV | 3.1779 | 1.1879 | 159.7% | With 7.36kW EVSE + 3.68kWH Battery storage + 3kW PV | 3.1568 | 1.0868 | 158.6%
75 | 3.757 | 0.087 | 2.316% |  |  |  | 75 | 11.4233 | 0.28002 | 2.451% |  |  |  | With 3.68kW HP + 3.68kWH Battery storage + 3kW PV | 2.0046 | 0.074647 | 103.9% | Same as C V33 | With 3.68kW HP + 3.68kWH Battery storage + 3kW PV | 5.2028 | 1.0928 | 126.6% | With 3.68kW HP + 3.68kWH Battery storage + 3kW PV | 2.417 | 0.61702 | 134.3% | With 3.68kW HP + 3.68kWH Battery storage + 3kW PV | 1.8602 | -0.12977 | 93.48% | With 3.68kW HP + 3.68kWH Battery storage + 3kW PV | 1.7985 | -0.27154 | 90.37%
100 | 3.732 | 0.062 | 1.661% |  |  |  | 100 | 11.4334 | 0.1799 | 1.573% |  |  |  | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage +3kW PV | 4.2682 | 2.3382 | 221.1% |  | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage +3kW PV | 9.5275 | 5.4175 | 231.8% | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage +3kW PV | 4.7863 | 2.9863 | 265.9% | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage +3kW PV | 4.0851 | 2.0951 | 205.3% | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage +3kW PV | 4.003 | 1.933 | 201.2%
ADMD Calc 7.36kW EVSE + House
Customers | Mean | St Dev | St Dev % | [17 empty] | 1 coefficients |  |  |  | 25 coefficients |  |  |  | 75 coefficients |  |  |  | 100 coefficients
1 | 10.307 | 1.2866 | 12.48% | [17 empty] | 3.4275 |  |  |  | 1.4992 |  |  |  | 1.6608 |  |  |  | 1.7217
25 | 5.6367 | 0.51892 | 9.206% | [12 empty] | 50 coefficients |  |  |  | 1.753 | 0.67617 |  |  | 2.1918 | 0.47227 |  |  | 1.8851 | 0.43978 |  |  | 1.8064 | 0.43315
50 | 5.4351 | 0.21443 | 3.945% | [12 empty] | 1.6075 | Differnce in starting ADMD for Batt vs NPG Paper |  |  | 2.506 | 0.96661 |  |  | 3.1332 | 0.67513 |  |  | 2.6948 | 0.62868 |  |  | 2.5823 | 0.6192
75 | 5.3708 | 0.12437 | 2.316% | [11 empty] | 1.971 | 0.4484 | Ratio of EV 3.68 kW to HP kW for Cust |  |  | 2.5925 | 1.6854 |  |  | 4.6409 | 1.3862 |  |  | 4.2865 | 1.3372 |  |  | 4.1704 | 1.327
100 | 5.3351 | 0.088632 | 1.661% | [11 empty] | 2.8176 | 0.64101 | Ratio of EV 7.36 kW to HP kW for Cust |  |  | 4.3695 |  |  |  | 6.4333 |  |  |  | 5.7317 |  |  |  | 5.5341
[15 empty] | 4.3955 | 1.3503 | Ratio of EV 7.36 kW + HP kW to HPkW for Cust
5.9352
EV |  |  |  | HP | HP + EV |  | 0.84158 | DR Factor EV
3.097 | Diff House to 3.68EV | [6 empty] | DR Factor EV
1.8286 | R 1 to 25 |  |  | 1.2772 | 1.5529 | R 1 to 25
1.0371 | R 25 to 50 |  |  | 0.98467 | 1.0109 | R 25 to 50
1.012 | R 50 to 75 |  |  | 0.99251 | 1.0022 | R 50 to 75
1.0067 | R75 to 100 |  |  | 0.99153 | 0.99911 | R75 to 100
ADMD
-
Note on L15: Haynes, Jack: 3.87 from 5kW HP normal continous

## HPC16N (hidden)
ADMD Calc 3.68kW EVSE Only | [6 empty] | ADMD Calc 3.68kW Heat Pump Only (obselete)
Customers | Mean | St Dev | St Dev % |  |  |  | Customers | Mean | St Dev | St Dev % |  |  |  | Increases at 50 customers (No Battery or PV) | ADMD | Addition vs Standard | % | 1.18 Factor due to differnce between EV HO and HP HO values from NPG | Increases at 1 customers (No Battery or PV) | ADMD | Addition vs Standard | % | Increases at 25 customers (No Battery or PV) | ADMD | Addition vs Standard | % | Increases at 75 customers (No Battery or PV) | ADMD | Addition vs Standard | % | Increases at 100 customers (No Battery or PV) | ADMD | Addition vs Standard | % | Variables | Options | Input
1 | 3.587 | 0.549 | 15.31% |  |  |  | 1 | 2.844 | 0.549 | 19.3% |  |  |  | House only | 1.929 | 0 | 0% |  | House only | 4.113 | 0 | 0% | House only | 1.799 | 0 | 0% | House only | 1.993 | 0 | 0% | House only | 2.066 | 0.137 | 0% | Number of Customers on Feeder ? | 1, 25, 50 or 100 | 25
25 | 3.756 | 0.021 | 0.5591% |  |  |  | 25 | 1.58 | 0.317 | 20.06% |  |  |  | With 3.68kW EVSE | 3.802 | 1.873 | 197.1% |  | With 3.68kW EVSE | 7.21 | 3.097 | 175.3% | With 3.68kW EVSE | 3.943 | 2.144 | 219.2% | With 3.68kW EVSE | 3.757 | 1.764 | 188.5% | With 3.68kW EVSE | 3.732 | 1.803 | 193.5% | Size of Charger ? | 0, 3.68 or 7.36 | 0
50 | 3.737 | 0.031 | 0.8295% |  |  |  | 50 | 1.389 | 0.192 | 13.82% |  |  |  | With 7.36kW (or two 3.68) EVSE | 5.4351 | 3.5061 | 281.8% |  | With 7.36kW (or two 3.68) EVSE | 10.307 | 6.194 | 250.6% | With 7.36kW (or two 3.68) EVSE | 5.6367 | 3.8377 | 313.3% | With 7.36kW (or two 3.68) EVSE | 5.3708 | 3.3778 | 269.5% | With 7.36kW (or two 3.68) EVSE | 5.3351 | 3.4061 | 276.6% | Heat Pump Installed ? | Yes or No | Yes
75 | 3.713 | 0.044 | 1.185% |  |  |  | 75 | 1.304 | 0.209 | 16.03% |  |  |  | With 3.68kW HP (10kW Heat Output) | 5.195 | 3.266 | 269.3% |  | With 3.68kW HP (10kW Heat Output) | 13.483 | 9.37 | 327.8% | With 3.68kW HP (10kW Heat Output) | 6.2637 | 4.4647 | 348.2% | With 3.68kW HP (10kW Heat Output) | 4.8207 | 2.8277 | 241.9% | With 3.68kW HP (10kW Heat Output) | 4.6607 | 2.7317 | 241.6% | Battery Storage ? | Yes or No | No
100 | 3.688 | 0.053 | 1.437% |  |  |  | 100 | 1.276 | 0.092 | 7.21% |  |  |  | With 3.68kW HP + 7.36kW EVSE | 9.3145 | 7.3855 | 482.9% |  | With 3.68kW HP + 7.36kW EVSE | 20.7919 | 16.6789 | 505.5% | With 3.68kW HP + 7.36kW EVSE | 10.4452 | 8.6462 | 580.6% | With 3.68kW HP + 7.36kW EVSE | 8.915 | 6.922 | 447.3% | With 3.68kW HP + 7.36kW EVSE | 8.7358 | 6.8068 | 452.9% | PV on Roof ? (Must have battery) | Yes or No | No
[35 empty] | Storage Heating Installed ? | Yes or No | No
[35 empty] | Extreme Outside Temp ? (T < - 5C) | Yes or No | Yes
[35 empty] | Is there a 60A current limitting device ? | Yes or No | No
ADMD Calc House only | [6 empty] | ADMD Calc 16kW (Heat) HP + House | [6 empty] | ADMD for 50 customers with Battery No PV | ADMD | Addition vs Standard | % |  | ADMD for 1 customers with Battery No PV | ADMD | Addition vs Standard | % | ADMD for 25 customers with Battery No PV | ADMD | Addition vs Standard | % | ADMD for 75 customers with Battery No PV | ADMD | Addition vs Standard | % | ADMD for 100 customers with Battery No PV | ADMD | Addition vs Standard | % |  | ADMD Normal Air Temp | 6.2637
Customers | Mean | St Dev | St Dev % |  |  |  | Customers | Mean | St Dev | St Dev % |  |  |  | House only | 1.93 | 0 | 0% |  | House only | 4.11 | 0 | 0% | House only | 1.8 | 0 | 0% | House only | 1.99 | 0 | 0% | House only | 2.07 | 0 | 0%
1 | 4.113 | 0.769 | 18.7% |  |  |  | 1 | 13.483 | 1.98 | 14.69% |  | 5.728 |  | With 3.68kWH Battery storage | 1.1767 | -0.75331 | 60.97% |  | With 3.68kWH Battery storage | 2.5089 | -1.6011 | 61.04% | With 3.68kWH Battery storage | 1.0974 | -0.70261 | 60.97% | With 3.68kWH Battery storage | 1.2157 | -0.77427 | 61.09% | With 3.68kWH Battery storage | 1.2603 | -0.80974 | 60.88% |  | ADMD Extreme Air Temp | 9.2077
25 | 1.799 | 0.343 | 19.07% |  |  |  | 25 | 6.2637 | 0.673 | 10.74% |  | 2.661 | 2.1526 | With 3.68kW EVSE + 3.68kWH Battery storage | 2.3192 | 0.38922 | 120.2% |  | With 3.68kW EVSE + 3.68kWH Battery storage | 4.3981 | 0.2881 | 107% | With 3.68kW EVSE + 3.68kWH Battery storage | 2.4052 | 0.60523 | 133.6% | With 3.68kW EVSE + 3.68kWH Battery storage | 2.2918 | 0.30177 | 115.2% | With 3.68kW EVSE + 3.68kWH Battery storage | 2.2765 | 0.20652 | 110%
50 | 1.929 | 0.358 | 18.56% |  |  |  | 50 | 5.195 | 0.387 | 7.449% |  | 2.207 | 1.2057 | With 7.36kW EVSE + 3.68kWH Battery storage | 3.3154 | 1.3854 | 171.8% |  | With 7.36kW EVSE + 3.68kWH Battery storage | 6.2873 | 2.1773 | 153% | With 7.36kW EVSE + 3.68kWH Battery storage | 3.4384 | 1.6384 | 191% | With 7.36kW EVSE + 3.68kWH Battery storage | 3.2762 | 1.2862 | 164.6% | With 7.36kW EVSE + 3.68kWH Battery storage | 3.2544 | 1.1844 | 157.2% |  | ADMD Current Limiter | 9.2077
75 | 1.993 | 0.311 | 15.6% |  |  |  | 75 | 4.8207 | 0.221 | 4.584% |  | 2.048 | 1.0776 | With 3.68kW HP + 3.68kWH Battery storage | 3.169 | 1.239 | 164.2% |  | With 3.68kW HP + 3.68kWH Battery storage | 8.2246 | 4.1146 | 200.1% | With 3.68kW HP + 3.68kWH Battery storage | 3.8208 | 2.0208 | 212.3% | With 3.68kW HP + 3.68kWH Battery storage | 2.9406 | 0.95065 | 147.8% | With 3.68kW HP + 3.68kWH Battery storage | 2.843 | 0.77301 | 137.3%
100 | 2.066 | 0.229 | 11.08% |  |  |  | 100 | 4.6607 | 0.128 | 2.746% |  | 1.98 | 1.0343 | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage | 5.6818 | 3.7518 | 294.4% |  | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage | 12.6831 | 8.5731 | 308.6% | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage | 6.3716 | 4.5716 | 354% | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage | 5.4382 | 3.4482 | 273.3% | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage | 5.3288 | 3.2588 | 257.4%
ADMD Calc 3.68kW EVSE + House | [6 empty] | ADMD Calc 16kW (Heat) HP + House + 7.36 kW EVSE | [6 empty] | ADMD for 50 customers with Battery and PV | ADMD | Addition vs Standard | % |  | ADMD for 1 customers with Battery and PV | ADMD | Addition vs Standard | % | ADMD for 25 customers with Battery and PV | ADMD | Addition vs Standard | % | ADMD for 75 customers with Battery and PV | ADMD | Addition vs Standard | % | ADMD for 100 customers with Battery and PV | ADMD | Addition vs Standard | %
Customers | Mean | St Dev | St Dev % |  |  |  | Customers | Mean | St Dev | St Dev % | 1.18 Factor due to differnce between EV HO and HP HO values from NPG |  |  | House only | 1.93 | 0 | 0% |  | House only | 4.11 | 0 | 0% | House only | 1.8 | 0 | 0% | House only | 1.99 | 0 | 0% | House only | 2.07 | 0 | 0%
1 | 7.21 | 0.9 | 12.48% |  |  |  | 1 | 20.7919 | 2.8244 | 13.58% |  |  |  | With 3.68kWH Battery storage +3kW PV | 1.1414 | -0.78861 | 59.14% |  | With 3.68kWH Battery storage +3kW PV | 2.4337 | -1.6763 | 59.21% | With 3.68kWH Battery storage +3kW PV | 1.0645 | -0.73553 | 59.14% | With 3.68kWH Battery storage +3kW PV | 1.1793 | -0.81074 | 59.26% | With 3.68kWH Battery storage +3kW PV | 1.2225 | -0.84755 | 61.43%
25 | 3.943 | 0.363 | 9.206% |  |  |  | 25 | 10.4452 | 1.0419 | 9.975% |  |  |  | With 3.68kW EVSE + 3.68kWH Battery storage + 3kW PV | 2.2496 | 0.31964 | 116.6% |  | With 3.68kW EVSE + 3.68kWH Battery storage + 3kW PV | 4.2662 | 0.15616 | 103.8% | With 3.68kW EVSE + 3.68kWH Battery storage + 3kW PV | 2.3331 | 0.53307 | 129.6% | With 3.68kW EVSE + 3.68kWH Battery storage + 3kW PV | 2.223 | 0.23302 | 111.7% | With 3.68kW EVSE + 3.68kWH Battery storage + 3kW PV | 2.2082 | 0.13822 | 111%
50 | 3.802 | 0.15 | 3.945% |  |  |  | 50 | 9.3145 | 0.53068 | 5.697% |  |  |  | With 7.36kW EVSE + 3.68kWH Battery storage + 3kW PV | 3.216 | 1.286 | 166.6% |  | With 7.36kW EVSE + 3.68kWH Battery storage + 3kW PV | 6.0987 | 1.9887 | 148.4% | With 7.36kW EVSE + 3.68kWH Battery storage + 3kW PV | 3.3352 | 1.5352 | 185.3% | With 7.36kW EVSE + 3.68kWH Battery storage + 3kW PV | 3.1779 | 1.1879 | 159.7% | With 7.36kW EVSE + 3.68kWH Battery storage + 3kW PV | 3.1568 | 1.0868 | 158.6%
75 | 3.757 | 0.087 | 2.316% |  |  |  | 75 | 8.915 | 0.30757 | 3.45% |  |  |  | With 3.68kW HP + 3.68kWH Battery storage + 3kW PV | 3.0739 | 1.1439 | 159.3% | Same as C V33 | With 3.68kW HP + 3.68kWH Battery storage + 3kW PV | 7.9779 | 3.8679 | 194.1% | With 3.68kW HP + 3.68kWH Battery storage + 3kW PV | 3.7062 | 1.9062 | 205.9% | With 3.68kW HP + 3.68kWH Battery storage + 3kW PV | 2.8524 | 0.86243 | 143.3% | With 3.68kW HP + 3.68kWH Battery storage + 3kW PV | 2.7577 | 0.68772 | 138.6%
100 | 3.732 | 0.062 | 1.661% |  |  |  | 100 | 8.7358 | 0.19252 | 2.204% |  |  |  | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage +3kW PV | 5.5114 | 3.5814 | 285.6% |  | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage +3kW PV | 12.3026 | 8.1926 | 299.3% | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage +3kW PV | 6.1804 | 4.3804 | 343.4% | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage +3kW PV | 5.275 | 3.285 | 265.1% | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage +3kW PV | 5.1689 | 3.0989 | 259.7%
ADMD Calc 7.36kW EVSE + House
Customers | Mean | St Dev | St Dev % | [17 empty] | 1 coefficients |  |  |  | 25 coefficients |  |  |  | 75 coefficients |  |  |  | 100 coefficients
1 | 10.307 | 1.2866 | 12.48% | [17 empty] | 3.4275 |  |  |  | 1.4992 |  |  |  | 1.6608 |  |  |  | 1.7217
25 | 5.6367 | 0.51892 | 9.206% | [12 empty] | 50 coefficients |  |  |  | 1.753 | 0.53475 |  |  | 2.1918 | 0.6295 |  |  | 1.8851 | 0.77934 |  |  | 1.8064 | 0.80074
50 | 5.4351 | 0.21443 | 3.945% | [12 empty] | 1.6075 | Differnce in starting ADMD for Batt vs NPG Paper |  |  | 2.506 | 0.76444 |  |  | 3.1332 | 0.8999 |  |  | 2.6948 | 1.1141 |  |  | 2.5823 | 1.1447
75 | 5.3708 | 0.12437 | 2.316% | [11 empty] | 1.971 | 0.73186 | Ratio of EV 3.68 kW to HP kW for Cust |  |  | 3.2781 | 1.5421 |  |  | 3.4817 | 1.6676 |  |  | 2.4188 | 1.8493 |  |  | 2.2559 | 1.8744
100 | 5.3351 | 0.088632 | 1.661% | [11 empty] | 2.8176 | 1.0462 | Ratio of EV 7.36 kW to HP kW for Cust |  |  | 5.0552 |  |  |  | 5.8061 |  |  |  | 4.4732 |  |  |  | 4.2283
[15 empty] | 2.6931 | 1.793 | Ratio of EV 7.36 kW + HP kW to HPkW for Cust
4.8287
EV |  |  |  | HP | HP + EV |  | 0.84158 | DR Factor EV
3.097 | Diff House to 3.68EV | [6 empty] | DR Factor EV
1.8286 | R 1 to 25 |  |  | 2.1526 | 1.9906 | R 1 to 25
1.0371 | R 25 to 50 |  |  | 1.2057 | 1.1214 | R 25 to 50
1.012 | R 50 to 75 |  |  | 1.0776 | 1.0448 | R 50 to 75
1.0067 | R75 to 100 |  |  | 1.0343 | 1.0205 | R75 to 100
ADMD
-
Note on L15: Haynes, Jack: 3.87 from 5kW HP normal continous

## HPC16PC (hidden)
ADMD Calc 3.68kW EVSE Only | [6 empty] | ADMD Calc 3.68kW Heat Pump Only (obselete)
Customers | Mean | St Dev | St Dev % |  |  |  | Customers | Mean | St Dev | St Dev % |  |  |  | Increases at 50 customers (No Battery or PV) | ADMD | Addition vs Standard | % | 1.18 Factor due to differnce between EV HO and HP HO values from NPG | Increases at 1 customers (No Battery or PV) | ADMD | Addition vs Standard | % | Increases at 25 customers (No Battery or PV) | ADMD | Addition vs Standard | % | Increases at 75 customers (No Battery or PV) | ADMD | Addition vs Standard | % | Increases at 100 customers (No Battery or PV) | ADMD | Addition vs Standard | % | Variables | Options | Input
1 | 3.587 | 0.549 | 15.31% |  |  |  | 1 | 2.844 | 0.549 | 19.3% |  |  |  | House only | 1.929 | 0 | 0% |  | House only | 4.113 | 0 | 0% | House only | 1.799 | 0 | 0% | House only | 1.993 | 0 | 0% | House only | 2.066 | 0.137 | 0% | Number of Customers on Feeder ? | 1, 25, 50 or 100 | 25
25 | 3.756 | 0.021 | 0.5591% |  |  |  | 25 | 1.58 | 0.317 | 20.06% |  |  |  | With 3.68kW EVSE | 3.802 | 1.873 | 197.1% |  | With 3.68kW EVSE | 7.21 | 3.097 | 175.3% | With 3.68kW EVSE | 3.943 | 2.144 | 219.2% | With 3.68kW EVSE | 3.757 | 1.764 | 188.5% | With 3.68kW EVSE | 3.732 | 1.803 | 193.5% | Size of Charger ? | 0, 3.68 or 7.36 | 0
50 | 3.737 | 0.031 | 0.8295% |  |  |  | 50 | 1.389 | 0.192 | 13.82% |  |  |  | With 7.36kW (or two 3.68) EVSE | 5.4351 | 3.5061 | 281.8% |  | With 7.36kW (or two 3.68) EVSE | 10.307 | 6.194 | 250.6% | With 7.36kW (or two 3.68) EVSE | 5.6367 | 3.8377 | 313.3% | With 7.36kW (or two 3.68) EVSE | 5.3708 | 3.3778 | 269.5% | With 7.36kW (or two 3.68) EVSE | 5.3351 | 3.4061 | 276.6% | Heat Pump Installed ? | Yes or No | Yes
75 | 3.713 | 0.044 | 1.185% |  |  |  | 75 | 1.304 | 0.209 | 16.03% |  |  |  | With 3.68kW HP (10kW Heat Output) | 17.7578 | 15.8288 | 920.6% |  | With 3.68kW HP (10kW Heat Output) | 20.3349 | 16.2219 | 494.4% | With 3.68kW HP (10kW Heat Output) | 14.919 | 13.12 | 829.3% | With 3.68kW HP (10kW Heat Output) | 17.8333 | 15.8403 | 894.8% | With 3.68kW HP (10kW Heat Output) | 17.9195 | 15.9905 | 929% | Battery Storage ? | Yes or No | No
100 | 3.688 | 0.053 | 1.437% |  |  |  | 100 | 1.276 | 0.092 | 7.21% |  |  |  | With 3.68kW HP + 7.36kW EVSE | 16.2202 | 14.2912 | 840.9% |  | With 3.68kW HP + 7.36kW EVSE | 24.5419 | 20.4289 | 596.7% | With 3.68kW HP + 7.36kW EVSE | 16.4509 | 14.6519 | 914.4% | With 3.68kW HP + 7.36kW EVSE | 16.1576 | 14.1646 | 810.7% | With 3.68kW HP + 7.36kW EVSE | 16.1423 | 14.2133 | 836.8% | PV on Roof ? (Must have battery) | Yes or No | No
[35 empty] | Storage Heating Installed ? | Yes or No | No
[35 empty] | Extreme Outside Temp ? (T < - 5C) | Yes or No | No
[35 empty] | Is there a 60A current limitting device ? | Yes or No | No
ADMD Calc House only | [6 empty] | ADMD Calc 16kW (Heat) HP + House | [6 empty] | ADMD for 50 customers with Battery No PV | ADMD | Addition vs Standard | % |  | ADMD for 1 customers with Battery No PV | ADMD | Addition vs Standard | % | ADMD for 25 customers with Battery No PV | ADMD | Addition vs Standard | % | ADMD for 75 customers with Battery No PV | ADMD | Addition vs Standard | % | ADMD for 100 customers with Battery No PV | ADMD | Addition vs Standard | % |  | ADMD Normal Air Temp | 14.919
Customers | Mean | St Dev | St Dev % |  |  |  | Customers | Mean | St Dev | St Dev % |  |  |  | House only | 1.93 | 0 | 0% |  | House only | 4.11 | 0 | 0% | House only | 1.8 | 0 | 0% | House only | 1.99 | 0 | 0% | House only | 2.07 | 0 | 0%
1 | 4.113 | 0.769 | 18.7% |  |  |  | 1 | 17.233 | 1.98 | 11.49% |  | 5.728 |  | With 3.68kWH Battery storage | 1.1767 | -0.75331 | 60.97% |  | With 3.68kWH Battery storage | 2.5089 | -1.6011 | 61.04% | With 3.68kWH Battery storage | 1.0974 | -0.70261 | 60.97% | With 3.68kWH Battery storage | 1.2157 | -0.77427 | 61.09% | With 3.68kWH Battery storage | 1.2603 | -0.80974 | 60.88% |  | ADMD Extreme Air Temp | 14.919
25 | 1.799 | 0.343 | 19.07% |  |  |  | 25 | 14.919 | 0.673 | 4.511% |  | 2.661 | 2.1526 | With 3.68kW EVSE + 3.68kWH Battery storage | 2.3192 | 0.38922 | 120.2% |  | With 3.68kW EVSE + 3.68kWH Battery storage | 4.3981 | 0.2881 | 107% | With 3.68kW EVSE + 3.68kWH Battery storage | 2.4052 | 0.60523 | 133.6% | With 3.68kW EVSE + 3.68kWH Battery storage | 2.2918 | 0.30177 | 115.2% | With 3.68kW EVSE + 3.68kWH Battery storage | 2.2765 | 0.20652 | 110%
50 | 1.929 | 0.358 | 18.56% |  |  |  | 50 | 15.049 | 0.387 | 2.572% |  | 2.207 | 1.2057 | With 7.36kW EVSE + 3.68kWH Battery storage | 3.3154 | 1.3854 | 171.8% |  | With 7.36kW EVSE + 3.68kWH Battery storage | 6.2873 | 2.1773 | 153% | With 7.36kW EVSE + 3.68kWH Battery storage | 3.4384 | 1.6384 | 191% | With 7.36kW EVSE + 3.68kWH Battery storage | 3.2762 | 1.2862 | 164.6% | With 7.36kW EVSE + 3.68kWH Battery storage | 3.2544 | 1.1844 | 157.2% |  | ADMD Current Limiter | 14.919
75 | 1.993 | 0.311 | 15.6% |  |  |  | 75 | 15.113 | 0.221 | 1.462% |  | 2.048 | 1.0776 | With 3.68kW HP + 3.68kWH Battery storage | 3.169 | 1.239 | 164.2% |  | With 3.68kW HP + 3.68kWH Battery storage | 8.2246 | 4.1146 | 200.1% | With 3.68kW HP + 3.68kWH Battery storage | 3.8208 | 2.0208 | 212.3% | With 3.68kW HP + 3.68kWH Battery storage | 2.9406 | 0.95065 | 147.8% | With 3.68kW HP + 3.68kWH Battery storage | 2.843 | 0.77301 | 137.3%
100 | 2.066 | 0.229 | 11.08% |  |  |  | 100 | 15.186 | 0.128 | 0.8429% |  | 1.98 | 1.0343 | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage | 5.6818 | 3.7518 | 294.4% |  | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage | 12.6831 | 8.5731 | 308.6% | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage | 6.3716 | 4.5716 | 354% | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage | 5.4382 | 3.4482 | 273.3% | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage | 5.3288 | 3.2588 | 257.4%
ADMD Calc 3.68kW EVSE + House | [6 empty] | ADMD Calc 16kW (Heat) HP + House + 7.36 kW EVSE | [6 empty] | ADMD for 50 customers with Battery and PV | ADMD | Addition vs Standard | % |  | ADMD for 1 customers with Battery and PV | ADMD | Addition vs Standard | % | ADMD for 25 customers with Battery and PV | ADMD | Addition vs Standard | % | ADMD for 75 customers with Battery and PV | ADMD | Addition vs Standard | % | ADMD for 100 customers with Battery and PV | ADMD | Addition vs Standard | %
Customers | Mean | St Dev | St Dev % |  |  |  | Customers | Mean | St Dev | St Dev % | 1.18 Factor due to differnce between EV HO and HP HO values from NPG |  |  | House only | 1.93 | 0 | 0% |  | House only | 4.11 | 0 | 0% | House only | 1.8 | 0 | 0% | House only | 1.99 | 0 | 0% | House only | 2.07 | 0 | 0%
1 | 7.21 | 0.9 | 12.48% |  |  |  | 1 | 24.5419 | 2.9416 | 11.99% |  |  |  | With 3.68kWH Battery storage +3kW PV | 1.1414 | -0.78861 | 59.14% |  | With 3.68kWH Battery storage +3kW PV | 2.4337 | -1.6763 | 59.21% | With 3.68kWH Battery storage +3kW PV | 1.0645 | -0.73553 | 59.14% | With 3.68kWH Battery storage +3kW PV | 1.1793 | -0.81074 | 59.26% | With 3.68kWH Battery storage +3kW PV | 1.2225 | -0.84755 | 61.43%
25 | 3.943 | 0.363 | 9.206% |  |  |  | 25 | 16.4509 | 1.1283 | 6.859% |  |  |  | With 3.68kW EVSE + 3.68kWH Battery storage + 3kW PV | 2.2496 | 0.31964 | 116.6% |  | With 3.68kW EVSE + 3.68kWH Battery storage + 3kW PV | 4.2662 | 0.15616 | 103.8% | With 3.68kW EVSE + 3.68kWH Battery storage + 3kW PV | 2.3331 | 0.53307 | 129.6% | With 3.68kW EVSE + 3.68kWH Battery storage + 3kW PV | 2.223 | 0.23302 | 111.7% | With 3.68kW EVSE + 3.68kWH Battery storage + 3kW PV | 2.2082 | 0.13822 | 111%
50 | 3.802 | 0.15 | 3.945% |  |  |  | 50 | 16.2202 | 0.52853 | 3.258% |  |  |  | With 7.36kW EVSE + 3.68kWH Battery storage + 3kW PV | 3.216 | 1.286 | 166.6% |  | With 7.36kW EVSE + 3.68kWH Battery storage + 3kW PV | 6.0987 | 1.9887 | 148.4% | With 7.36kW EVSE + 3.68kWH Battery storage + 3kW PV | 3.3352 | 1.5352 | 185.3% | With 7.36kW EVSE + 3.68kWH Battery storage + 3kW PV | 3.1779 | 1.1879 | 159.7% | With 7.36kW EVSE + 3.68kWH Battery storage + 3kW PV | 3.1568 | 1.0868 | 158.6%
75 | 3.757 | 0.087 | 2.316% |  |  |  | 75 | 16.1576 | 0.30522 | 1.889% |  |  |  | With 3.68kW HP + 3.68kWH Battery storage + 3kW PV | 3.0739 | 1.1439 | 159.3% | Same as C V33 | With 3.68kW HP + 3.68kWH Battery storage + 3kW PV | 7.9779 | 3.8679 | 194.1% | With 3.68kW HP + 3.68kWH Battery storage + 3kW PV | 3.7062 | 1.9062 | 205.9% | With 3.68kW HP + 3.68kWH Battery storage + 3kW PV | 2.8524 | 0.86243 | 143.3% | With 3.68kW HP + 3.68kWH Battery storage + 3kW PV | 2.7577 | 0.68772 | 138.6%
100 | 3.732 | 0.062 | 1.661% |  |  |  | 100 | 16.1423 | 0.20212 | 1.252% |  |  |  | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage +3kW PV | 5.5114 | 3.5814 | 285.6% |  | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage +3kW PV | 12.3026 | 8.1926 | 299.3% | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage +3kW PV | 6.1804 | 4.3804 | 343.4% | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage +3kW PV | 5.275 | 3.285 | 265.1% | With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage +3kW PV | 5.1689 | 3.0989 | 259.7%
ADMD Calc 7.36kW EVSE + House
Customers | Mean | St Dev | St Dev % | [17 empty] | 1 coefficients |  |  |  | 25 coefficients |  |  |  | 75 coefficients |  |  |  | 100 coefficients
1 | 10.307 | 1.2866 | 12.48% | [17 empty] | 3.4275 |  |  |  | 1.4992 |  |  |  | 1.6608 |  |  |  | 1.7217
25 | 5.6367 | 0.51892 | 9.206% | [12 empty] | 50 coefficients |  |  |  | 1.753 | 0.35456 |  |  | 2.1918 | 0.26429 |  |  | 1.8851 | 0.21067 |  |  | 1.8064 | 0.20826
50 | 5.4351 | 0.21443 | 3.945% | [12 empty] | 1.6075 | Differnce in starting ADMD for Batt vs NPG Paper |  |  | 2.506 | 0.50686 |  |  | 3.1332 | 0.37782 |  |  | 2.6948 | 0.30117 |  |  | 2.5823 | 0.29772
75 | 5.3708 | 0.12437 | 2.316% | [11 empty] | 1.971 | 0.2141 | Ratio of EV 3.68 kW to HP kW for Cust |  |  | 4.9441 | 1.2069 |  |  | 8.2929 | 1.1027 |  |  | 8.948 | 0.90603 |  |  | 8.6735 | 0.90083
100 | 5.3351 | 0.088632 | 1.661% | [11 empty] | 2.8176 | 0.30607 | Ratio of EV 7.36 kW to HP kW for Cust |  |  | 5.9669 |  |  |  | 9.1445 |  |  |  | 8.1072 |  |  |  | 7.8133
[15 empty] | 9.2057 | 0.91341 | Ratio of EV 7.36 kW + HP kW to HPkW for Cust
8.4086
EV |  |  |  | HP | HP + EV |  | 0.84158 | DR Factor EV
3.097 | Diff House to 3.68EV | [6 empty] | DR Factor EV
1.8286 | R 1 to 25 |  |  | 1.1551 | 1.4918 | R 1 to 25
1.0371 | R 25 to 50 |  |  | 0.99136 | 1.0142 | R 25 to 50
1.012 | R 50 to 75 |  |  | 0.99577 | 1.0039 | R 50 to 75
1.0067 | R75 to 100 |  |  | 0.99519 | 1.0009 | R75 to 100
ADMD
-
Note on L15: Haynes, Jack: 3.87 from 5kW HP normal continous

## HPBatt8KW (hidden)
LCTs at Property |  |  | Battery Data |  | S = 14 kWh |  | LCTs at Property |  |  | Battery Data |  | S = 14 kWh |  |  | LCTs at Property |  |  | Battery Data |  | S = 14 kWh |  | LCTs at Property |  |  | Battery Data |  | S = 14 kwh
Standalone |  |  | Max Y = | 1.23 | C = 3.68 kW/h Max | D= 5kW/h Max | 8kW HP Norm |  |  | Max Y = | 2.1 | C = 3.68 kW/h Max | D= 5kW/h Max |  | With 7.36kW EVSE |  |  | Max Y = | 3.5 | C = 3.68 kW/h Max | D= 5kW/h Max | With 7.36kW EVSE + 8 KW HP |  |  | Max Y = | 3.45 | C = 3.68 kW/h Max | D= 5kW/h Max
[7 empty] | 1.695 | [7 empty] | 2.82 | [6 empty] | 2.85
Hour | Time | AHHD (G) | ADMD | Load | Available Charge (kWh) | Cuml. Batt Charge (kWh) | Hour | Time | AHHD (G) | ADMD | Load | Available Charge (kWh) | Cuml. Batt Charge (kWh) |  | Hour | Time | AHHD (G) | ADMD | Load | Available Charge (kWh) | Cuml. Batt Charge (kWh) | Hour | Time | AHHD (G) | ADMD | Load | Available Charge (kWh) | Cuml. Batt Charge (kWh)
0 | 0:00 | 0.1 | 0.25 | 1.23 | 0.98 | 0.98 | 0 | 0:00 | 0.1 | 0.42375 | 2.1 | 1.6763 | 1.6763 |  | 0 | 0:00 | 0.1 | 0.705 | 3.5 | 2.795 | 2.795 | 0 | 0:00 | 0.1 | 0.7125 | 3.45 | 2.7375 | 2.7375 | 3.45
1 | 1:00 | 0.2 | 0.5 | 1.23 | 0.73 | 1.71 | 1 | 1:00 | 0.2 | 0.8475 | 2.1 | 1.2525 | 2.9287 |  | 1 | 1:00 | 0.2 | 1.41 | 3.5 | 2.09 | 4.885 | 1 | 1:00 | 0.2 | 1.425 | 3.45 | 2.025 | 4.7625 | 3.45
2 | 2:00 | 0.15 | 0.375 | 1.23 | 0.855 | 2.565 | 2 | 2:00 | 0.15 | 0.63562 | 2.1 | 1.4644 | 4.3931 |  | 2 | 2:00 | 0.15 | 1.0575 | 3.5 | 2.4425 | 7.3275 | 2 | 2:00 | 0.15 | 1.0688 | 3.45 | 2.3813 | 7.1438 | 3.45
3 | 3:00 | 0.15 | 0.375 | 1.23 | 0.855 | 3.42 | 3 | 3:00 | 0.15 | 0.63562 | 2.1 | 1.4644 | 5.8575 |  | 3 | 3:00 | 0.15 | 1.0575 | 3.5 | 2.4425 | 9.77 | 3 | 3:00 | 0.15 | 1.0688 | 3.45 | 2.3813 | 9.525 | 3.45
4 | 4:00 | 0.15 | 0.375 | 1.23 | 0.855 | 4.275 | 4 | 4:00 | 0.15 | 0.63562 | 2.1 | 1.4644 | 7.3219 |  | 4 | 4:00 | 0.15 | 1.0575 | 3.5 | 2.4425 | 12.2125 | 4 | 4:00 | 0.15 | 1.0688 | 3.45 | 2.3813 | 11.9062 | 3.45
5 | 5:00 | 0.175 | 0.4375 | 1.23 | 0.7925 | 5.0675 | 5 | 5:00 | 0.175 | 0.74156 | 2.1 | 1.3584 | 8.6803 |  | 5 | 5:00 | 0.175 | 1.2337 | 3.5 | 2.2663 | 14.4787 | 5 | 5:00 | 0.175 | 1.2469 | 3.45 | 2.2031 | 14.1094 | 3.45
6 | 6:00 | 0.2 | 0.5 | 1.23 | 0.73 | 5.7975 | 6 | 6:00 | 0.2 | 0.8475 | 2.1 | 1.2525 | 9.9328 |  | 6 | 6:00 | 0.2 | 1.41 | 3.5 | 2.09 | 16.5687 | 6 | 6:00 | 0.2 | 1.425 | 3.45 | 2.025 | 16.1344 | 3.45
7 | 7:00 | 0.4 | 1 | 1.23 | 0.23 | 6.0275 | 7 | 7:00 | 0.4 | 1.695 | 2.1 | 0.405 | 10.3378 |  | 7 | 7:00 | 0.4 | 2.82 | 3.5 | 0.68 | 17.2487 | 7 | 7:00 | 0.4 | 2.85 | 3.45 | 0.6 | 16.7344 | 3.45 | PV Agg Input (kWh)
8 | 8:00 | 0.6 | 1.5 | 1.23 | -0.27 | 5.7575 | 8 | 8:00 | 0.6 | 2.5425 | 2.1 | -0.4425 | 9.8953 |  | 8 | 8:00 | 0.6 | 4.23 | 3.5 | -0.73 | 16.5187 | 8 | 8:00 | 0.6 | 4.275 | 3.45 | -0.825 | 15.9094 | 3.45 | 8:00 | 0.3
9 | 9:00 | 0.6 | 1.5 | 1.23 | -0.27 | 5.4875 | 9 | 9:00 | 0.6 | 2.5425 | 2.1 | -0.4425 | 9.4528 |  | 9 | 9:00 | 0.6 | 4.23 | 3.5 | -0.73 | 15.7887 | 9 | 9:00 | 0.6 | 4.275 | 3.45 | -0.825 | 15.0844 | 3.45 | 9:00 | 0.3
10 | 10:00 | 0.55 | 1.375 | 1.23 | -0.145 | 5.3425 | 10 | 10:00 | 0.55 | 2.3306 | 2.1 | -0.23062 | 9.2222 |  | 10 | 10:00 | 0.55 | 3.8775 | 3.5 | -0.3775 | 15.4112 | 10 | 10:00 | 0.55 | 3.9188 | 3.45 | -0.46875 | 14.6156 | 3.45 | 10:00 | 0.3
11 | 11:00 | 0.5 | 1.25 | 1.23 | -0.02 | 5.3225 | 11 | 11:00 | 0.5 | 2.1187 | 2.1 | -0.01875 | 9.2034 |  | 11 | 11:00 | 0.5 | 3.525 | 3.5 | -0.025 | 15.3862 | 11 | 11:00 | 0.5 | 3.5625 | 3.45 | -0.1125 | 14.5031 | 3.45 | 11:00 | 0.3
12 | 12:00 | 0.5 | 1.25 | 1.23 | -0.02 | 5.3025 | 12 | 12:00 | 0.5 | 2.1187 | 2.1 | -0.01875 | 9.1847 |  | 12 | 12:00 | 0.5 | 3.525 | 3.5 | -0.025 | 15.3612 | 12 | 12:00 | 0.5 | 3.5625 | 3.45 | -0.1125 | 14.3906 | 3.45 | 12:00 | 0.3
13 | 13:00 | 0.5 | 1.25 | 1.23 | -0.02 | 5.2825 | 13 | 13:00 | 0.5 | 2.1187 | 2.1 | -0.01875 | 9.1659 |  | 13 | 13:00 | 0.5 | 3.525 | 3.5 | -0.025 | 15.3362 | 13 | 13:00 | 0.5 | 3.5625 | 3.45 | -0.1125 | 14.2781 | 3.45 | 13:00 | 0.3
14 | 14:00 | 0.5 | 1.25 | 1.23 | -0.02 | 5.2625 | 14 | 14:00 | 0.5 | 2.1187 | 2.1 | -0.01875 | 9.1472 |  | 14 | 14:00 | 0.5 | 3.525 | 3.5 | -0.025 | 15.3112 | 14 | 14:00 | 0.5 | 3.5625 | 3.45 | -0.1125 | 14.1656 | 3.45 | 14:00 | 0.3
15 | 15:00 | 0.5 | 1.25 | 1.23 | -0.02 | 5.2425 | 15 | 15:00 | 0.5 | 2.1187 | 2.1 | -0.01875 | 9.1284 |  | 15 | 15:00 | 0.5 | 3.525 | 3.5 | -0.025 | 15.2862 | 15 | 15:00 | 0.5 | 3.5625 | 3.45 | -0.1125 | 14.0531 | 3.45 | 15:00 | 0.3
16 | 16:00 | 0.6 | 1.5 | 1.23 | -0.27 | 4.9725 | 16 | 16:00 | 0.6 | 2.5425 | 2.1 | -0.4425 | 8.6859 |  | 16 | 16:00 | 0.6 | 4.23 | 3.5 | -0.73 | 14.5562 | 16 | 16:00 | 0.6 | 4.275 | 3.45 | -0.825 | 13.2281 | 3.45 | 16:00 | 0.3
17 | 17:00 | 0.7 | 1.75 | 1.23 | -0.52 | 4.4525 | 17 | 17:00 | 0.7 | 2.9663 | 2.1 | -0.86625 | 7.8197 |  | 17 | 17:00 | 0.7 | 4.935 | 3.5 | -1.435 | 13.1212 | 17 | 17:00 | 0.7 | 4.9875 | 3.45 | -1.5375 | 11.6906 | 3.45 | Total PV contribution | 2.7
18 | 18:00 | 0.8 | 2 | 1.23 | -0.77 | 3.6825 | 18 | 18:00 | 0.8 | 3.39 | 2.1 | -1.29 | 6.5297 |  | 18 | 18:00 | 0.8 | 5.64 | 3.5 | -2.14 | 10.9812 | 18 | 18:00 | 0.8 | 5.7 | 3.45 | -2.25 | 9.4406 | 3.45 | Per Hour reduction (24H) | 0.1125
19 | 19:00 | 0.8 | 2 | 1.23 | -0.77 | 2.9125 | 19 | 19:00 | 0.8 | 3.39 | 2.1 | -1.29 | 5.2397 |  | 19 | 19:00 | 0.8 | 5.64 | 3.5 | -2.14 | 8.8412 | 19 | 19:00 | 0.8 | 5.7 | 3.45 | -2.25 | 7.1906 | 3.45 | New Threshold | 3.3375
20 | 20:00 | 0.8 | 2 | 1.23 | -0.77 | 2.1425 | 20 | 20:00 | 0.8 | 3.39 | 2.1 | -1.29 | 3.9497 |  | 20 | 20:00 | 0.8 | 5.64 | 3.5 | -2.14 | 6.7012 | 20 | 20:00 | 0.8 | 5.7 | 3.45 | -2.25 | 4.9406 | 3.45 | Percentage Total | 96.74%
21 | 21:00 | 0.8 | 2 | 1.23 | -0.77 | 1.3725 | 21 | 21:00 | 0.8 | 3.39 | 2.1 | -1.29 | 2.6597 |  | 21 | 21:00 | 0.8 | 5.64 | 3.5 | -2.14 | 4.5612 | 21 | 21:00 | 0.8 | 5.7 | 3.45 | -2.25 | 2.6906 | 3.45
22 | 22:00 | 0.6 | 1.5 | 1.23 | -0.27 | 1.1025 | 22 | 22:00 | 0.6 | 2.5425 | 2.1 | -0.4425 | 2.2172 |  | 22 | 22:00 | 0.6 | 4.23 | 3.5 | -0.73 | 3.8312 | 22 | 22:00 | 0.6 | 4.275 | 3.45 | -0.825 | 1.8656 | 3.45
23 | 23:00 | 0.4 | 1 | 1.23 | 0.23 | 1.3325 | 23 | 23:00 | 0.4 | 1.695 | 2.1 | 0.405 | 2.6222 |  | 23 | 23:00 | 0.4 | 2.82 | 3.5 | 0.68 | 4.5112 | 23 | 23:00 | 0.4 | 2.85 | 3.45 | 0.6 | 2.4656 | 3.45
[5 empty] | % Peak Shaved | 38.5% | [5 empty] | % Peak Shaved | 38.05% | [6 empty] | % Peak Shaved | 37.94% | [5 empty] | % Peak Shaved | 39.47%
[5 empty] | Capacity Needed | 6.0275 | [5 empty] | Capacity Needed | 10.3378 | [6 empty] | Capacity Needed | 17.2487 | [5 empty] | Capacity Needed | 16.7344
[5 empty] | Max Charge Rate | 0.98 | [5 empty] | Max Charge Rate | 1.6763 | [6 empty] | Max Charge Rate | 2.795 | [5 empty] | Max Charge Rate | 2.7375
[5 empty] | Max Discharge Rate | -0.77 | [5 empty] | Max Discharge Rate | -1.29 | [6 empty] | Max Discharge Rate | -2.14 | [5 empty] | Max Discharge Rate | -2.25
Cs = 50
[7 empty] | LCTs at Property |  |  | Battery Data |  | S = 14 kWh | Draw of HP KW | 4.68 | [7 empty] | LCTs at Property |  |  | Battery Data |  | S = 14 kwh | Draw of HP KW | 4.68
[7 empty] | 8kW POWER CUT |  |  | Max Y = | 2.1 | C = 3.68 kW/h Max | D= 5kW/h Max | [8 empty] | With 7.36kW EVSE + HP POWC |  |  | Y= | 4.4 | C = 3.68 kW/h Max | D= 5kW/h Max
[7 empty] | 1.695 | [14 empty] | 3.605
[7 empty] | Hour | Time | AHHD (G) | ADMD | Load | Available Charge (kWh) | Cuml. Batt Charge (kWh) | BackUp Batt Charge (kWh) | [7 empty] | Hour | Time | AHHD (G) | ADMD | Load | Available Charge (kWh) | Cuml. Batt Charge (kWh) | BackUp Batt Charge (kWh)
[7 empty] | 0 | 0:00 | 0.1 | 0.42375 | 2.1 | 1.6763 | 1.6763 | 15.7162 | [7 empty] | 0 | 0:00 | 0.1 | 0.90125 | 4.4 | 3.4988 | 3.4988 | 17.5388
[7 empty] | 1 | 1:00 | 0.2 | 0.8475 | 2.1 | 1.2525 | 5.5509 | 19.5909 | [7 empty] | 1 | 1:00 | 0.2 | 1.8025 | 4.4 | 2.5975 | 6.0963 | 20.1363
[7 empty] | 2 | 2:00 | 0.15 | 0.63562 | 2.1 | 1.4644 | 7.0153 | 21.0553 | [7 empty] | 2 | 2:00 | 0.15 | 1.3519 | 4.4 | 3.0481 | 9.1444 | 23.1844
[7 empty] | 3 | 3:00 | 0.15 | 0.63562 | 2.1 | 1.4644 | 8.4797 | 22.5197 | [7 empty] | 3 | 3:00 | 0.15 | 1.3519 | 4.4 | 3.0481 | 12.1925 | 26.2325
[7 empty] | 4 | 4:00 | 0.15 | 0.63562 | 2.1 | 1.4644 | 9.9441 | 23.9841 | [7 empty] | 4 | 4:00 | 0.15 | 1.3519 | 4.4 | 3.0481 | 15.2406 | 29.2806
[7 empty] | 5 | 5:00 | 0.175 | 0.74156 | 2.1 | 1.3584 | 11.3025 | 25.3425 | [7 empty] | 5 | 5:00 | 0.175 | 1.5772 | 4.4 | 2.8228 | 18.0634 | 32.1034
[7 empty] | 6 | 6:00 | 0.2 | 0.8475 | 2.1 | 1.2525 | 12.555 | 26.595 | [7 empty] | 6 | 6:00 | 0.2 | 1.8025 | 4.4 | 2.5975 | 20.6609 | 34.7009
[7 empty] | 7 | 7:00 | 0.4 | 1.695 | 2.1 | 0.405 | 12.96 | 27 | [7 empty] | 7 | 7:00 | 0.4 | 3.605 | 4.4 | 0.795 | 21.4559 | 35.4959
[7 empty] | 8 | 8:00 | 0.6 | 2.5425 | 2.1 | -0.4425 | 12.5175 | 26.5575 | [7 empty] | 8 | 8:00 | 0.6 | 5.4075 | 4.4 | -1.0075 | 20.4484 | 34.4884
[7 empty] | 9 | 9:00 | 0.6 | 2.5425 | 2.1 | -0.4425 | 12.075 | 26.115 | [7 empty] | 9 | 9:00 | 0.6 | 5.4075 | 4.4 | -1.0075 | 19.4409 | 33.4809
[7 empty] | 10 | 10:00 | 0.55 | 2.3306 | 2.1 | -0.23062 | 11.8444 | 25.8844 | [7 empty] | 10 | 10:00 | 0.55 | 4.9569 | 4.4 | -0.55687 | 18.8841 | 32.9241
[7 empty] | 11 | 11:00 | 0.5 | 2.1187 | 2.1 | -0.01875 | 11.8256 | 25.8656 | [7 empty] | 11 | 11:00 | 0.5 | 4.5062 | 4.4 | -0.10625 | 18.7778 | 32.8178
[7 empty] | 12 | 12:00 | 0.5 | 2.1187 | 2.1 | -0.01875 | 11.8069 | 25.8469 | [7 empty] | 12 | 12:00 | 0.5 | 4.5062 | 4.4 | -0.10625 | 18.6716 | 32.7116
[7 empty] | 13 | 13:00 | 0.5 | 2.1187 | 2.1 | -0.01875 | 11.7881 | 25.8281 | [7 empty] | 13 | 13:00 | 0.5 | 4.5062 | 4.4 | -0.10625 | 18.5653 | 32.6053
[7 empty] | 14 | 14:00 | 0.5 | 2.1187 | 2.1 | -0.01875 | 11.7694 | 25.8094 | [7 empty] | 14 | 14:00 | 0.5 | 4.5062 | 4.4 | -0.10625 | 18.4591 | 32.4991
[7 empty] | 15 | 15:00 | 0.5 | 2.1187 | 2.1 | -0.01875 | 11.7506 | 25.7906 | [7 empty] | 15 | 15:00 | 0.5 | 4.5062 | 4.4 | -0.10625 | 18.3528 | 32.3928
[7 empty] | 16 | 16:00 | 0.6 | 2.5425 | 2.1 | -0.4425 | 11.3081 | 25.3481 | [7 empty] | 16 | 16:00 | 0.6 | 5.4075 | 4.4 | -1.0075 | 17.3453 | 31.3853
[7 empty] | 17 | 17:00 | 0.7 | 2.9663 | 2.1 | -0.86625 | 10.4419 | 24.4819 | [7 empty] | 17 | 17:00 | 0.7 | 6.3087 | 4.4 | -1.9087 | 15.4366 | 29.4766
[7 empty] | 18 | 18:00 | 0.8 | 3.39 | 2.1 | -1.29 | 9.1519 | 23.1919 | [7 empty] | 18 | 18:00 | 0.8 | 7.21 | 4.4 | -2.81 | 12.6266 | 26.6666
[7 empty] | 19 | 19:00 | 0.8 | 3.39 | 2.1 | -1.29 | 7.8619 | 21.9019 | [7 empty] | 19 | 19:00 | 0.8 | 7.21 | 4.4 | -2.81 | 9.8166 | 23.8566
[7 empty] | 20 | 20:00 | 0.8 | 3.39 | 2.1 | -1.29 | 6.5719 | 20.6119 | [7 empty] | 20 | 20:00 | 0.8 | 7.21 | 4.4 | -2.81 | 7.0066 | 21.0466
[7 empty] | 21 | 21:00 | 0.8 | 3.39 | 2.1 | -1.29 | 5.2819 | 19.3219 | [7 empty] | 21 | 21:00 | 0.8 | 7.21 | 4.4 | -2.81 | 4.1966 | 18.2366
[7 empty] | 22 | 22:00 | 0.6 | 2.5425 | 2.1 | -0.4425 | 4.8394 | 18.8794 | [7 empty] | 22 | 22:00 | 0.6 | 5.4075 | 4.4 | -1.0075 | 3.1891 | 17.2291
[7 empty] | 23 | 23:00 | 0.4 | 1.695 | 2.1 | 0.405 | 5.2444 | 19.2844 | [7 empty] | 23 | 23:00 | 0.4 | 3.605 | 4.4 | 0.795 | 3.9841 | 18.0241
[12 empty] | % Peak Shaved | 38.05% | [13 empty] | % Peak Shaved | 38.97%
[12 empty] | Capacity Needed | 12.96 | 27 | [12 empty] | Capacity Needed | 21.4559 | 35.4959
[12 empty] | Max Charge Rate | 1.6763 | [13 empty] | Max Charge Rate | 3.4988
[12 empty] | Max Discharge Rate | -1.29 | [13 empty] | Max Discharge Rate | -2.81

## HPBatt16KW (hidden)
LCTs at Property |  |  | Battery Data |  | S = 14 kWh |  | LCTs at Property |  |  | Battery Data |  | S = 14 kWh |  |  | LCTs at Property |  |  | Battery Data |  | S = 14 kWh |  | LCTs at Property |  |  | Battery Data |  | S = 14 kwh
Standalone |  |  | Max Y = | 1.23 | C = 3.68 kW/h Max | D= 5kW/h Max | 16kW HP Norm |  |  | Max Y = | 3.2 | C = 3.68 kW/h Max | D= 5kW/h Max |  | With 7.36kW EVSE |  |  | Max Y = | 3.5 | C = 3.68 kW/h Max | D= 5kW/h Max | With 7.36kW EVSE + 8 KW HP |  |  | Max Y = | 5.7 | C = 3.68 kW/h Max | D= 5kW/h Max
[7 empty] | 2.6 | [7 empty] | 2.82 | [6 empty] | 4.655
Hour | Time | AHHD (G) | ADMD | Load | Available Charge (kWh) | Cuml. Batt Charge (kWh) | Hour | Time | AHHD (G) | ADMD | Load | Available Charge (kWh) | Cuml. Batt Charge (kWh) |  | Hour | Time | AHHD (G) | ADMD | Load | Available Charge (kWh) | Cuml. Batt Charge (kWh) | Hour | Time | AHHD (G) | ADMD | Load | Available Charge (kWh) | Cuml. Batt Charge (kWh)
0 | 0:00 | 0.1 | 0.25 | 1.23 | 0.98 | 0.98 | 0 | 0:00 | 0.1 | 0.65 | 3.2 | 2.55 | 2.55 |  | 0 | 0:00 | 0.1 | 0.705 | 3.5 | 2.795 | 2.795 | 0 | 0:00 | 0.1 | 1.1638 | 5.7 | 4.5362 | 4.5362 | 5.7
1 | 1:00 | 0.2 | 0.5 | 1.23 | 0.73 | 1.71 | 1 | 1:00 | 0.2 | 1.3 | 3.2 | 1.9 | 4.45 |  | 1 | 1:00 | 0.2 | 1.41 | 3.5 | 2.09 | 4.885 | 1 | 1:00 | 0.2 | 2.3275 | 5.7 | 3.3725 | 7.9087 | 5.7
2 | 2:00 | 0.15 | 0.375 | 1.23 | 0.855 | 2.565 | 2 | 2:00 | 0.15 | 0.975 | 3.2 | 2.225 | 6.675 |  | 2 | 2:00 | 0.15 | 1.0575 | 3.5 | 2.4425 | 7.3275 | 2 | 2:00 | 0.15 | 1.7456 | 5.7 | 3.9544 | 11.8631 | 5.7
3 | 3:00 | 0.15 | 0.375 | 1.23 | 0.855 | 3.42 | 3 | 3:00 | 0.15 | 0.975 | 3.2 | 2.225 | 8.9 |  | 3 | 3:00 | 0.15 | 1.0575 | 3.5 | 2.4425 | 9.77 | 3 | 3:00 | 0.15 | 1.7456 | 5.7 | 3.9544 | 15.8175 | 5.7
4 | 4:00 | 0.15 | 0.375 | 1.23 | 0.855 | 4.275 | 4 | 4:00 | 0.15 | 0.975 | 3.2 | 2.225 | 11.125 |  | 4 | 4:00 | 0.15 | 1.0575 | 3.5 | 2.4425 | 12.2125 | 4 | 4:00 | 0.15 | 1.7456 | 5.7 | 3.9544 | 19.7719 | 5.7
5 | 5:00 | 0.175 | 0.4375 | 1.23 | 0.7925 | 5.0675 | 5 | 5:00 | 0.175 | 1.1375 | 3.2 | 2.0625 | 13.1875 |  | 5 | 5:00 | 0.175 | 1.2337 | 3.5 | 2.2663 | 14.4787 | 5 | 5:00 | 0.175 | 2.0366 | 5.7 | 3.6634 | 23.4353 | 5.7
6 | 6:00 | 0.2 | 0.5 | 1.23 | 0.73 | 5.7975 | 6 | 6:00 | 0.2 | 1.3 | 3.2 | 1.9 | 15.0875 |  | 6 | 6:00 | 0.2 | 1.41 | 3.5 | 2.09 | 16.5687 | 6 | 6:00 | 0.2 | 2.3275 | 5.7 | 3.3725 | 26.8078 | 5.7
7 | 7:00 | 0.4 | 1 | 1.23 | 0.23 | 6.0275 | 7 | 7:00 | 0.4 | 2.6 | 3.2 | 0.6 | 15.6875 |  | 7 | 7:00 | 0.4 | 2.82 | 3.5 | 0.68 | 17.2487 | 7 | 7:00 | 0.4 | 4.655 | 5.7 | 1.045 | 27.8528 | 5.7 | PV Agg Input (kWh)
8 | 8:00 | 0.6 | 1.5 | 1.23 | -0.27 | 5.7575 | 8 | 8:00 | 0.6 | 3.9 | 3.2 | -0.7 | 14.9875 |  | 8 | 8:00 | 0.6 | 4.23 | 3.5 | -0.73 | 16.5187 | 8 | 8:00 | 0.6 | 6.9825 | 5.7 | -1.2825 | 26.5703 | 5.7 | 8:00 | 0.3
9 | 9:00 | 0.6 | 1.5 | 1.23 | -0.27 | 5.4875 | 9 | 9:00 | 0.6 | 3.9 | 3.2 | -0.7 | 14.2875 |  | 9 | 9:00 | 0.6 | 4.23 | 3.5 | -0.73 | 15.7887 | 9 | 9:00 | 0.6 | 6.9825 | 5.7 | -1.2825 | 25.2878 | 5.7 | 9:00 | 0.3
10 | 10:00 | 0.55 | 1.375 | 1.23 | -0.145 | 5.3425 | 10 | 10:00 | 0.55 | 3.575 | 3.2 | -0.375 | 13.9125 |  | 10 | 10:00 | 0.55 | 3.8775 | 3.5 | -0.3775 | 15.4112 | 10 | 10:00 | 0.55 | 6.4006 | 5.7 | -0.70063 | 24.5872 | 5.7 | 10:00 | 0.3
11 | 11:00 | 0.5 | 1.25 | 1.23 | -0.02 | 5.3225 | 11 | 11:00 | 0.5 | 3.25 | 3.2 | -0.05 | 13.8625 |  | 11 | 11:00 | 0.5 | 3.525 | 3.5 | -0.025 | 15.3862 | 11 | 11:00 | 0.5 | 5.8188 | 5.7 | -0.11875 | 24.4684 | 5.7 | 11:00 | 0.3
12 | 12:00 | 0.5 | 1.25 | 1.23 | -0.02 | 5.3025 | 12 | 12:00 | 0.5 | 3.25 | 3.2 | -0.05 | 13.8125 |  | 12 | 12:00 | 0.5 | 3.525 | 3.5 | -0.025 | 15.3612 | 12 | 12:00 | 0.5 | 5.8188 | 5.7 | -0.11875 | 24.3497 | 5.7 | 12:00 | 0.3
13 | 13:00 | 0.5 | 1.25 | 1.23 | -0.02 | 5.2825 | 13 | 13:00 | 0.5 | 3.25 | 3.2 | -0.05 | 13.7625 |  | 13 | 13:00 | 0.5 | 3.525 | 3.5 | -0.025 | 15.3362 | 13 | 13:00 | 0.5 | 5.8188 | 5.7 | -0.11875 | 24.2309 | 5.7 | 13:00 | 0.3
14 | 14:00 | 0.5 | 1.25 | 1.23 | -0.02 | 5.2625 | 14 | 14:00 | 0.5 | 3.25 | 3.2 | -0.05 | 13.7125 |  | 14 | 14:00 | 0.5 | 3.525 | 3.5 | -0.025 | 15.3112 | 14 | 14:00 | 0.5 | 5.8188 | 5.7 | -0.11875 | 24.1122 | 5.7 | 14:00 | 0.3
15 | 15:00 | 0.5 | 1.25 | 1.23 | -0.02 | 5.2425 | 15 | 15:00 | 0.5 | 3.25 | 3.2 | -0.05 | 13.6625 |  | 15 | 15:00 | 0.5 | 3.525 | 3.5 | -0.025 | 15.2862 | 15 | 15:00 | 0.5 | 5.8188 | 5.7 | -0.11875 | 23.9934 | 5.7 | 15:00 | 0.3
16 | 16:00 | 0.6 | 1.5 | 1.23 | -0.27 | 4.9725 | 16 | 16:00 | 0.6 | 3.9 | 3.2 | -0.7 | 12.9625 |  | 16 | 16:00 | 0.6 | 4.23 | 3.5 | -0.73 | 14.5562 | 16 | 16:00 | 0.6 | 6.9825 | 5.7 | -1.2825 | 22.7109 | 5.7 | 16:00 | 0.3
17 | 17:00 | 0.7 | 1.75 | 1.23 | -0.52 | 4.4525 | 17 | 17:00 | 0.7 | 4.55 | 3.2 | -1.35 | 11.6125 |  | 17 | 17:00 | 0.7 | 4.935 | 3.5 | -1.435 | 13.1212 | 17 | 17:00 | 0.7 | 8.1463 | 5.7 | -2.4463 | 20.2647 | 5.7 | Total PV contribution | 2.7
18 | 18:00 | 0.8 | 2 | 1.23 | -0.77 | 3.6825 | 18 | 18:00 | 0.8 | 5.2 | 3.2 | -2 | 9.6125 |  | 18 | 18:00 | 0.8 | 5.64 | 3.5 | -2.14 | 10.9812 | 18 | 18:00 | 0.8 | 9.31 | 5.7 | -3.61 | 16.6547 | 5.7 | Per Hour reduction (24H) | 0.1125
19 | 19:00 | 0.8 | 2 | 1.23 | -0.77 | 2.9125 | 19 | 19:00 | 0.8 | 5.2 | 3.2 | -2 | 7.6125 |  | 19 | 19:00 | 0.8 | 5.64 | 3.5 | -2.14 | 8.8412 | 19 | 19:00 | 0.8 | 9.31 | 5.7 | -3.61 | 13.0447 | 5.7 | New Threshold | 5.5875
20 | 20:00 | 0.8 | 2 | 1.23 | -0.77 | 2.1425 | 20 | 20:00 | 0.8 | 5.2 | 3.2 | -2 | 5.6125 |  | 20 | 20:00 | 0.8 | 5.64 | 3.5 | -2.14 | 6.7012 | 20 | 20:00 | 0.8 | 9.31 | 5.7 | -3.61 | 9.4347 | 5.7 | Percentage Total | 98.03%
21 | 21:00 | 0.8 | 2 | 1.23 | -0.77 | 1.3725 | 21 | 21:00 | 0.8 | 5.2 | 3.2 | -2 | 3.6125 |  | 21 | 21:00 | 0.8 | 5.64 | 3.5 | -2.14 | 4.5612 | 21 | 21:00 | 0.8 | 9.31 | 5.7 | -3.61 | 5.8247 | 5.7
22 | 22:00 | 0.6 | 1.5 | 1.23 | -0.27 | 1.1025 | 22 | 22:00 | 0.6 | 3.9 | 3.2 | -0.7 | 2.9125 |  | 22 | 22:00 | 0.6 | 4.23 | 3.5 | -0.73 | 3.8312 | 22 | 22:00 | 0.6 | 6.9825 | 5.7 | -1.2825 | 4.5422 | 5.7
23 | 23:00 | 0.4 | 1 | 1.23 | 0.23 | 1.3325 | 23 | 23:00 | 0.4 | 2.6 | 3.2 | 0.6 | 3.5125 |  | 23 | 23:00 | 0.4 | 2.82 | 3.5 | 0.68 | 4.5112 | 23 | 23:00 | 0.4 | 4.655 | 5.7 | 1.045 | 5.5872 | 5.7
[5 empty] | % Peak Shaved | 38.5% | [5 empty] | % Peak Shaved | 38.46% | [6 empty] | % Peak Shaved | 37.94% | [5 empty] | % Peak Shaved | 38.78%
[5 empty] | Capacity Needed | 6.0275 | [5 empty] | Capacity Needed | 15.6875 | [6 empty] | Capacity Needed | 17.2487 | [5 empty] | Capacity Needed | 27.8528
[5 empty] | Max Charge Rate | 0.98 | [5 empty] | Max Charge Rate | 2.55 | [6 empty] | Max Charge Rate | 2.795 | [5 empty] | Max Charge Rate | 4.5362
[5 empty] | Max Discharge Rate | -0.77 | [5 empty] | Max Discharge Rate | -2 | [6 empty] | Max Discharge Rate | -2.14 | [5 empty] | Max Discharge Rate | -3.61
Cs = 50
[7 empty] | LCTs at Property |  |  | Battery Data |  | S = 14 kWh | Draw of HP KW | 9.37 | [7 empty] | LCTs at Property |  |  | Battery Data |  | S = 14 kwh | Draw of HP KW | 9.37
[7 empty] | 16kW POWER CUT |  |  | Max Y = | 3.2 | C = 3.68 kW/h Max | D= 5kW/h Max | [8 empty] | With 7.36kW EVSE + HP POWC |  |  | Y= | 5.7 | C = 3.68 kW/h Max | D= 5kW/h Max
[7 empty] | 2.6 | [14 empty] | 4.655
[7 empty] | Hour | Time | AHHD (G) | ADMD | Load | Available Charge (kWh) | Cuml. Batt Charge (kWh) | BackUp Batt Charge (kWh) | [7 empty] | Hour | Time | AHHD (G) | ADMD | Load | Available Charge (kWh) | Cuml. Batt Charge (kWh) | BackUp Batt Charge (kWh)
[7 empty] | 0 | 0:00 | 0.1 | 0.65 | 3.2 | 2.55 | 2.55 | 30.66 | [7 empty] | 0 | 0:00 | 0.1 | 1.1638 | 5.7 | 4.5362 | 4.5362 | 32.6463
[7 empty] | 1 | 1:00 | 0.2 | 1.3 | 3.2 | 1.9 | 4.45 | 32.56 | [7 empty] | 1 | 1:00 | 0.2 | 2.3275 | 5.7 | 3.3725 | 7.9087 | 36.0187
[7 empty] | 2 | 2:00 | 0.15 | 0.975 | 3.2 | 2.225 | 6.675 | 34.785 | [7 empty] | 2 | 2:00 | 0.15 | 1.7456 | 5.7 | 3.9544 | 11.8631 | 39.9731
[7 empty] | 3 | 3:00 | 0.15 | 0.975 | 3.2 | 2.225 | 8.9 | 37.01 | [7 empty] | 3 | 3:00 | 0.15 | 1.7456 | 5.7 | 3.9544 | 15.8175 | 43.9275
[7 empty] | 4 | 4:00 | 0.15 | 0.975 | 3.2 | 2.225 | 11.125 | 39.235 | [7 empty] | 4 | 4:00 | 0.15 | 1.7456 | 5.7 | 3.9544 | 19.7719 | 47.8819
[7 empty] | 5 | 5:00 | 0.175 | 1.1375 | 3.2 | 2.0625 | 13.1875 | 41.2975 | [7 empty] | 5 | 5:00 | 0.175 | 2.0366 | 5.7 | 3.6634 | 23.4353 | 51.5453
[7 empty] | 6 | 6:00 | 0.2 | 1.3 | 3.2 | 1.9 | 15.0875 | 43.1975 | [7 empty] | 6 | 6:00 | 0.2 | 2.3275 | 5.7 | 3.3725 | 26.8078 | 54.9178
[7 empty] | 7 | 7:00 | 0.4 | 2.6 | 3.2 | 0.6 | 15.6875 | 43.7975 | [7 empty] | 7 | 7:00 | 0.4 | 4.655 | 5.7 | 1.045 | 27.8528 | 55.9628
[7 empty] | 8 | 8:00 | 0.6 | 3.9 | 3.2 | -0.7 | 14.9875 | 43.0975 | [7 empty] | 8 | 8:00 | 0.6 | 6.9825 | 5.7 | -1.2825 | 26.5703 | 54.6803
[7 empty] | 9 | 9:00 | 0.6 | 3.9 | 3.2 | -0.7 | 14.2875 | 42.3975 | [7 empty] | 9 | 9:00 | 0.6 | 6.9825 | 5.7 | -1.2825 | 25.2878 | 53.3978
[7 empty] | 10 | 10:00 | 0.55 | 3.575 | 3.2 | -0.375 | 13.9125 | 42.0225 | [7 empty] | 10 | 10:00 | 0.55 | 6.4006 | 5.7 | -0.70063 | 24.5872 | 52.6972
[7 empty] | 11 | 11:00 | 0.5 | 3.25 | 3.2 | -0.05 | 13.8625 | 41.9725 | [7 empty] | 11 | 11:00 | 0.5 | 5.8188 | 5.7 | -0.11875 | 24.4684 | 52.5784
[7 empty] | 12 | 12:00 | 0.5 | 3.25 | 3.2 | -0.05 | 13.8125 | 41.9225 | [7 empty] | 12 | 12:00 | 0.5 | 5.8188 | 5.7 | -0.11875 | 24.3497 | 52.4597
[7 empty] | 13 | 13:00 | 0.5 | 3.25 | 3.2 | -0.05 | 13.7625 | 41.8725 | [7 empty] | 13 | 13:00 | 0.5 | 5.8188 | 5.7 | -0.11875 | 24.2309 | 52.3409
[7 empty] | 14 | 14:00 | 0.5 | 3.25 | 3.2 | -0.05 | 13.7125 | 41.8225 | [7 empty] | 14 | 14:00 | 0.5 | 5.8188 | 5.7 | -0.11875 | 24.1122 | 52.2222
[7 empty] | 15 | 15:00 | 0.5 | 3.25 | 3.2 | -0.05 | 13.6625 | 41.7725 | [7 empty] | 15 | 15:00 | 0.5 | 5.8188 | 5.7 | -0.11875 | 23.9934 | 52.1034
[7 empty] | 16 | 16:00 | 0.6 | 3.9 | 3.2 | -0.7 | 12.9625 | 41.0725 | [7 empty] | 16 | 16:00 | 0.6 | 6.9825 | 5.7 | -1.2825 | 22.7109 | 50.8209
[7 empty] | 17 | 17:00 | 0.7 | 4.55 | 3.2 | -1.35 | 11.6125 | 39.7225 | [7 empty] | 17 | 17:00 | 0.7 | 8.1463 | 5.7 | -2.4463 | 20.2647 | 48.3747
[7 empty] | 18 | 18:00 | 0.8 | 5.2 | 3.2 | -2 | 9.6125 | 37.7225 | [7 empty] | 18 | 18:00 | 0.8 | 9.31 | 5.7 | -3.61 | 16.6547 | 44.7647
[7 empty] | 19 | 19:00 | 0.8 | 5.2 | 3.2 | -2 | 7.6125 | 35.7225 | [7 empty] | 19 | 19:00 | 0.8 | 9.31 | 5.7 | -3.61 | 13.0447 | 41.1547
[7 empty] | 20 | 20:00 | 0.8 | 5.2 | 3.2 | -2 | 5.6125 | 33.7225 | [7 empty] | 20 | 20:00 | 0.8 | 9.31 | 5.7 | -3.61 | 9.4347 | 37.5447
[7 empty] | 21 | 21:00 | 0.8 | 5.2 | 3.2 | -2 | 3.6125 | 31.7225 | [7 empty] | 21 | 21:00 | 0.8 | 9.31 | 5.7 | -3.61 | 5.8247 | 33.9347
[7 empty] | 22 | 22:00 | 0.6 | 3.9 | 3.2 | -0.7 | 2.9125 | 31.0225 | [7 empty] | 22 | 22:00 | 0.6 | 6.9825 | 5.7 | -1.2825 | 4.5422 | 32.6522
[7 empty] | 23 | 23:00 | 0.4 | 2.6 | 3.2 | 0.6 | 3.5125 | 31.6225 | [7 empty] | 23 | 23:00 | 0.4 | 4.655 | 5.7 | 1.045 | 5.5872 | 33.6972
[12 empty] | % Peak Shaved | 38.46% | [13 empty] | % Peak Shaved | 38.78%
[12 empty] | Capacity Needed | 15.6875 | 43.7975 | [12 empty] | Capacity Needed | 27.8528 | 55.9628
[12 empty] | Max Charge Rate | 2.55 | [13 empty] | Max Charge Rate | 4.5362
[12 empty] | Max Discharge Rate | -2 | [13 empty] | Max Discharge Rate | -3.61

## SPEN ADMD Calculator
Variables | Options / Ranges | User Input | User Input (3-4 Bedroom) | User Input (5+ Bedroom) |  |  | Standard Conditions Air Source | [8 empty] | Cold Load Pickup Conditions Air Source
Number of Customers on Feeder ? | 20 to 100 | 100 | 40 | 40
How many have EV Chargers ? | 0 to Number of Customers | 0 | 35 | 35 |  |  |  | 100 | 50 | 25 | 20 | 15 | 10 | 5 | 1 |  | 100 | 50 | 25 | 20 | 15 | 10 | 5 | 1
How many have EV Chargers AND Heat Pumps ? | 0 to Number of Customers | 0 | 35 | 35 |  |  |  | 100 | 50 | 25 | 20 | [5 empty] | 100 | 50 | 25 | 20
Do EV Chargers have Smart Charging (or are 3.68kW) ? | Yes or No | No | No | No |  |  | House only | 1.8 | 1.93 | 2.07 | 2.4 | 2.8 | 3.8 | 5.3 | 7.11 | House only | 1.8 | 1.93 | 2.07 | 2.2 | 2.8 | 3.8 | 5.3 | 7.11
How many have Air Source Heat Pumps ? | 0 to Number of Customers | 0 | 25 | 25 |  |  | With 3.68kW EVSE (No smart Charging (SC)) | 3.732 | 3.8 | 3.94 | 4.29 | 4.63 | 5.99 | 8.05 | 10.79 | With 3.68kW EVSE (No smart Charging (SC)) | 3.732 | 3.8 | 3.94 | 4.29 | 4.63 | 5.99 | 8.05 | 10.79
Average size of ASHP? (kW Heat) | 0, 5, 8 or 16 | 8 | 8 | 8 |  |  | With 7.36kW (or two 3.68) EVSE (No smart charging) | 4.35 | 4.58 | 4.92 | 5.05 | 6.52 | 8.289 | 10.938 | 14.47 | With 7.36kW (or two 3.68) EVSE (No smart charging) | 5.3351 | 5.44 | 5.64 | 6.081 | 6.52 | 8.289 | 10.938 | 14.47
How many have Ground Source Heat Pumps ? | 0 to Number of Customers | 0 | 10 | 10 |  |  | With 7.36kW (or two 3.68) EVSE (With smart charging) | 3.55 | 3.68 | 3.82 | 4.35 | 4.88 | 7.02 | 10.21 | 14.47 | With 7.36kW (or two 3.68) EVSE (With smart charging) | 3.732 | 3.8 | 3.94 | 4.29 | 4.88 | 7.02 | 10.21 | 14.47
Average size of GSHP? (kW Heat) | 0, 5, 8 or 16 | 16 | 16 | 16 |  |  | With 5kW (Heat Output) Heat Pump | 3.34 | 3.42 | 3.52 | 3.55 | 3.776 | 5.268 | 7.506 | 10.493 | With 5kW (Heat Output) Heat Pump | 5.18 | 5.31 | 5.45 | 5.7 | 5.95 | 6.96 | 8.47 | 10.493
How many have Hybrid Heat Pumps ? | 0 to Number of Customers | 0 | 10 | 10 |  |  | With 5kW (Heat Output) Heat Pump + 7.36kW EVSE (No SC) | 6.46 | 6.74 | 7.12 | 7.25 | 7.536 | 9.828 | 13.266 | 17.85 | With 5kW (Heat Output) Heat Pump + 7.36kW EVSE (No SC) | 8.31 | 8.33 | 8.36 | 8.83 | 9.31 | 11.21 | 14.05 | 17.85
Average size of HyHP? (kW Heat) | 0, 5, 8 or 16 | 5 | 5 | 5 |  |  | With 5kW (Heat Output) Heat Pump + 7.36kW EVSE (With SC) | 5.09 | 5.17 | 5.27 | 5.4335 | 6.087 | 8.701 | 12.622 | 17.85 | With 5kW (Heat Output) Heat Pump + 7.36kW EVSE (With SC) | 3.732 | 3.8 | 3.94 | 4.29 | 8.27 | 10.39 | 13.59 | 17.85
How many have storage heating ? | 0 to Number of Customers | 0 | 0 | 0 |  |  | With 8kW (Heat Output) Heat Pump | 4.42 | 4.52 | 4.64 | 4.7 | 5.038 | 6.954 | 9.828 | 13.663 | With 8kW (Heat Output) Heat Pump | 8.35 | 8.48 | 8.62 | 8.87 | 9.12 | 10.13 | 11.64 | 13.663
Average size of Storage Heating? (kW Elec) | 0, 5, 8 or 16 | 8 | 8 | 8 |  |  | With 8kW (Heat Output) Heat Pump + 7.36kW EVSE (No SC) | 7.54 | 7.84 | 8.24 | 8.7365 | 9.383 | 11.969 | 15.848 | 21.02 | With 8kW (Heat Output) Heat Pump + 7.36kW EVSE (No SC) | 11.43 | 11.45 | 11.57 | 12.04 | 12.52 | 14.41 | 17.24 | 21.02
How many have battery storage? |  | kW Output | 0 | 0 |  |  | With 8kW (Heat Output) Heat Pump + 7.36kW EVSE (With SC) | 6.17 | 6.27 | 6.39 | 6.5895 | 7.349 | 10.387 | 14.944 | 21.02 | With 8kW (Heat Output) Heat Pump + 7.36kW EVSE (With SC) | 3.732 | 3.8 | 3.94 | 4.29 | 11.44 | 13.57 | 16.76 | 21.02
How many have a 60A current limiting device ? | Average HH ADMD Standard | 1.8 |  |  |  |  | With 16kW (Heat Output) Heat Pump | 7.3 | 7.46 | 7.68 | 7.75 | 7.657 | 10.451 | 14.642 | 20.233 | With 16kW (Heat Output) Heat Pump | 14.92 | 15.05 | 15.19 | 15.44 | 15.69 | 16.7 | 18.21 | 20.233
| Total Feeder ADMD Standard | 180 |  |  |  |  | With 16kW (Heat Output) Heat Pump + 7.36kW EVSE (No SC) | 10.42 | 10.78 | 11.28 | 11.45 | 12.164 | 15.592 | 20.734 | 27.59 | With 16kW (Heat Output) Heat Pump + 7.36kW EVSE (No SC) | 17.92 | 18.05 | 18.19 | 18.66 | 19.13 | 21.01 | 23.83 | 27.59
| Average HH ADMD Cold Load | 1.8 |  |  |  |  | With 16kW (Heat Output) Heat Pump + 7.36kW EVSE (With SC) | 9.05 | 9.21 | 9.43 | 8.989 | 9.968 | 13.884 | 19.758 | 27.59 | With 16kW (Heat Output) Heat Pump + 7.36kW EVSE (With SC) | 3.732 | 3.8 | 3.94 | 4.29 | 18.01 | 20.14 | 23.33 | 27.59
| Total Feeder ADMD Cold Load | 180
[9 empty] | 51 | [6 empty] | Ground Source |  | 51
Ground Source
[8 empty] | 100 | 50 | 25 | 20 | 15 | 10 | 5 | 1 |  | 100 | 50 | 25 | 20 | 15 | 10 | 5 | 1
[7 empty] | House only | 1.8 | 1.93 | 2.07 | 2.4 | 2.8 | 3.8 | 5.3 | 7.11 | House only | 1.8 | 1.93 | 2.07 | 2.2 | 2.8 | 3.8 | 5.3 | 7.11
[7 empty] | With 3.68kW EVSE (No smart Charging (SC)) | 3.732 | 3.8 | 3.94 | 4.29 | 4.63 | 5.99 | 8.05 | 10.79 | With 3.68kW EVSE (No smart Charging (SC)) | 3.732 | 3.8 | 3.94 | 4.29 | 4.63 | 5.99 | 8.05 | 10.79
[7 empty] | With 7.36kW (or two 3.68) EVSE (No smart charging) | 4.35 | 4.58 | 4.92 | 5.05 | 6.52 | 8.289 | 10.938 | 14.47 | With 7.36kW (or two 3.68) EVSE (No smart charging) | 5.3351 | 5.44 | 5.64 | 6.081 | 6.52 | 8.289 | 10.938 | 14.47
| Standard | Cold Load Pickup | Standard | Cold Load Pickup | Standard | Cold Load Pickup | With 7.36kW (or two 3.68) EVSE (With smart charging) | 3.55 | 3.68 | 3.82 | 4.35 | 4.88 | 7.02 | 10.21 | 14.47 | With 7.36kW (or two 3.68) EVSE (With smart charging) | 3.732 | 3.8 | 3.94 | 4.29 | 4.88 | 7.02 | 10.21 | 14.47
Establish Diversity Level | 100 | 100 | 25 | 25 | 25 | 25 | With 5kW (Heat Output) Heat Pump | 3.34 | 3.42 | 3.52 | 3.55 | 3.4331 | 4.7895 | 6.8243 | 9.54 | With 5kW (Heat Output) Heat Pump | 4.23 | 4.36 | 4.5 | 4.63 | 5.23 | 6.23 | 7.73 | 9.54
Calculate EV Total | 0 | 0 | 172.2 | 172.2 | 172.2 | 172.2 | With 5kW (Heat Output) Heat Pump + 7.36kW EVSE (No SC) | 6.46 | 6.74 | 7.12 | 7.25 | 7.1931 | 9.3495 | 12.5843 | 16.9 | With 5kW (Heat Output) Heat Pump + 7.36kW EVSE (No SC) | 7.7651 | 7.87 | 8.07 | 8.5115 | 8.953 | 10.719 | 13.368 | 16.9
Calculate Non Smart Charge Value | 0 | 0 | 172.2 | 172.2 | 172.2 | 172.2 | With 5kW (Heat Output) Heat Pump + 7.36kW EVSE (With SC) | 5.09 | 5.17 | 5.27 | 5.4335 | 5.7441 | 8.2225 | 11.9403 | 16.9 | With 5kW (Heat Output) Heat Pump + 7.36kW EVSE (With SC) | 3.732 | 3.8 | 3.94 | 4.29 | 7.315 | 9.445 | 12.64 | 16.9
Calculate Smart Charge Value | 0 | 0 | 133.7 | 133.7 | 133.7 | 133.7 | With 8kW (Heat Output) Heat Pump | 4.14 | 4.24 | 4.36 | 4.4 | 3.9261 | 5.4774 | 7.8043 | 10.91 | With 8kW (Heat Output) Heat Pump | 5.6 | 5.73 | 5.87 | 6 | 6.6 | 7.6 | 9.1 | 10.91
Is Smart Charging Present ? | No | No | No | No | No | No | With 8kW (Heat Output) Heat Pump + 7.36kW EVSE (No SC) | 7.26 | 7.54 | 7.96 | 8.1 | 8.2711 | 10.4924 | 13.8243 | 18.27 | With 8kW (Heat Output) Heat Pump + 7.36kW EVSE (No SC) | 9.1351 | 9.24 | 9.44 | 9.8815 | 10.323 | 12.089 | 14.738 | 18.27
Calculate ASHP Total | 0 | 0 | 116 | 215.5 | 116 | 215.5 | With 8kW (Heat Output) Heat Pump + 7.36kW EVSE (With SC) | 5.89 | 5.99 | 6.11 | 6.5895 | 6.2371 | 8.9104 | 12.9203 | 18.27 | With 8kW (Heat Output) Heat Pump + 7.36kW EVSE (With SC) | 3.732 | 3.8 | 3.94 | 4.29 | 8.685 | 10.815 | 14.01 | 18.27
Calculate 5kW ASHP Total | 0 | 0 | 0 | 0 | 0 | 0 | With 16kW (Heat Output) Heat Pump | 5.99 | 6.12 | 6.32 | 6.4 | 4.8977 | 6.8329 | 9.7357 | 13.61 | With 16kW (Heat Output) Heat Pump | 8.3 | 8.43 | 8.57 | 8.7 | 9.3 | 10.3 | 11.8 | 13.61
Calculate 8kW ASHP Total | 0 | 0 | 116 | 215.5 | 116 | 215.5 | With 16kW (Heat Output) Heat Pump + 7.36kW EVSE (No SC) | 9.11 | 9.44 | 9.88 | 10.1 | 9.4047 | 11.9739 | 15.8277 | 20.97 | With 16kW (Heat Output) Heat Pump + 7.36kW EVSE (No SC) | 11.8351 | 11.94 | 12.14 | 12.5815 | 13.023 | 14.789 | 17.438 | 20.97
Calculate 16kW ASHP Total | 0 | 0 | 0 | 0 | 0 | 0 | With 16kW (Heat Output) Heat Pump + 7.36kW EVSE (With SC) | 7.74 | 7.87 | 8.07 | 8.989 | 7.2087 | 10.2659 | 14.8517 | 20.97 | With 16kW (Heat Output) Heat Pump + 7.36kW EVSE (With SC) | 3.732 | 3.8 | 3.94 | 4.29 | 11.385 | 13.515 | 16.71 | 20.97
Calculate GSHP Total | 0 | 0 | 63.2 | 85.7 | 63.2 | 85.7
Calculate 5kW GSHP Total | 0 | 0 | 0 | 0 | 0 | 0 | Hybrid | [8 empty] | Hybrid
Calculate 8kW GSHP Total | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 50 | 25 | 20 |  |  |  | 1 |  | 100 | 50 | 25 | 20 | 15 | 10 | 5 | 1
Calculate 16kW GSHP Total | 0 | 0 | 63.2 | 85.7 | 63.2 | 85.7 | House only | 1.8 | 1.93 | 2.07 | 2.4 | 2.8 | 3.8 | 5.3 | 7.11 | House only | 1.8 | 1.93 | 2.07 | 2.2 | 2.8 | 3.8 | 5.3 | 7.11
Calculate Hybrid Total | 0 | 0 | 25.2 | 32.9 | 25.2 | 32.9 | With 3.68kW EVSE (No smart Charging (SC)) | 3.732 | 3.8 | 3.94 | 4.29 | 4.63 | 5.99 | 8.05 | 10.79 | With 3.68kW EVSE (No smart Charging (SC)) | 3.732 | 3.8 | 3.94 | 4.29 | 4.63 | 5.99 | 8.05 | 10.79
Calculate 5kW Hybrid Total | 0 | 0 | 25.2 | 32.9 | 25.2 | 32.9 | With 7.36kW (or two 3.68) EVSE (No smart charging) | 4.35 | 4.58 | 4.92 | 5.05 | 6.52 | 8.289 | 10.938 | 14.47 | With 7.36kW (or two 3.68) EVSE (No smart charging) | 5.3351 | 5.44 | 5.64 | 6.081 | 6.52 | 8.289 | 10.938 | 14.47
Calculate 8kW Hybrid Total | 0 | 0 | 0 | 0 | 0 | 0 | With 7.36kW (or two 3.68) EVSE (With smart charging) | 3.55 | 3.68 | 3.82 | 4.35 | 4.88 | 7.02 | 10.21 | 14.47 | With 7.36kW (or two 3.68) EVSE (With smart charging) | 3.732 | 3.8 | 3.94 | 4.29 | 4.88 | 7.02 | 10.21 | 14.47
Calculate 16kW Hybrid Total | 0 | 0 | 0 | 0 | 0 | 0 | With 5kW (Heat Output) Heat Pump | 2.38 | 2.44 | 2.52 | 2.55 | 2.9976 | 4.1821 | 5.9587 | 8.33 | With 5kW (Heat Output) Heat Pump | 3.02 | 3.15 | 3.29 | 3.542 | 3.794 | 4.802 | 6.314 | 8.33
Calculate Storage Heating Total | 0 | 0 | 0 | 0 | 0 | 0 | With 5kW (Heat Output) Heat Pump + 7.36kW EVSE (No SC) | 5.5 | 5.74 | 6.12 | 6.25 | 6.7576 | 8.7421 | 11.7187 | 15.69 | With 5kW (Heat Output) Heat Pump + 7.36kW EVSE (No SC) | 6.5551 | 6.66 | 6.86 | 7.3015 | 7.743 | 9.509 | 12.158 | 15.69
Calculate 5kW Storage Total | 0 | 0 | 0 | 0 | 0 | 0 | With 5kW (Heat Output) Heat Pump + 7.36kW EVSE (With SC) | 4.13 | 4.19 | 4.27 | 5.4335 | 5.3086 | 7.6151 | 11.0747 | 15.69 | With 5kW (Heat Output) Heat Pump + 7.36kW EVSE (With SC) | 3.732 | 3.8 | 3.94 | 4.29 | 5.115 | 7.465 | 10.99 | 15.69
Calculate 8kW Storage Total | 0 | 0 | 0 | 0 | 0 | 0 | With 8kW (Heat Output) Heat Pump | 3.38 | 3.46 | 3.56 | 3.6 | 3.5266 | 4.9201 | 7.0103 | 9.8 | With 8kW (Heat Output) Heat Pump | 4.49 | 4.62 | 4.76 | 5.012 | 5.264 | 6.272 | 7.784 | 9.8
Calculate 16kW Storage Total | 0 | 0 | 0 | 0 | 0 | 0 | With 8kW (Heat Output) Heat Pump + 7.36kW EVSE (No SC) | 6.5 | 6.78 | 7.16 | 7.3 | 7.8716 | 9.9351 | 13.0303 | 17.16 | With 8kW (Heat Output) Heat Pump + 7.36kW EVSE (No SC) | 8.0251 | 8.13 | 8.33 | 8.7715 | 9.213 | 10.979 | 13.628 | 17.16
Calculate Standalone Households Total (No LCTs) | 180 | 180 | -10.35 | -10.35 | -10.35 | -10.35 | With 8kW (Heat Output) Heat Pump + 7.36kW EVSE (With SC) | 5.13 | 5.21 | 5.31 | 6.5895 | 5.8376 | 8.3531 | 12.1263 | 17.16 | With 8kW (Heat Output) Heat Pump + 7.36kW EVSE (With SC) | 3.732 | 3.8 | 3.94 | 4.29 | 5.262 | 7.906 | 11.872 | 17.16
Sub Total | 180 | 180 | 366.25 | 495.95 | 366.25 | 495.95 | With 16kW (Heat Output) Heat Pump | 4.67 | 4.78 | 4.92 | 5 | 4.2032 | 5.8639 | 8.3551 | 11.68 | With 16kW (Heat Output) Heat Pump | 6.37 | 6.5 | 6.64 | 6.892 | 7.144 | 8.152 | 9.664 | 11.68
EV + HP Number | 0 | 0 | 35 | 35 | 35 | 35 | With 16kW (Heat Output) Heat Pump + 7.36kW EVSE (No SC) | 7.79 | 8.08 | 8.52 | 8.7 | 8.7102 | 11.0049 | 14.4471 | 19.04 | With 16kW (Heat Output) Heat Pump + 7.36kW EVSE (No SC) | 9.9051 | 10.01 | 10.21 | 10.6515 | 11.093 | 12.859 | 15.508 | 19.04
Reduce load by required level Sub Total 2 | 180 | 180 | 293.8 | 423.5 | 293.8 | 423.5 | With 16kW (Heat Output) Heat Pump + 7.36kW EVSE (With SC) | 6.42 | 6.53 | 6.67 | 8.989 | 6.5142 | 9.2969 | 13.4711 | 19.04 | With 16kW (Heat Output) Heat Pump + 7.36kW EVSE (With SC) | 3.732 | 3.8 | 3.94 | 4.29 | 5.45 | 8.47 | 13 | 19.04
Calculate Battery ADMD Reduction Effect | #REF! | #REF! | 293.8 | 423.5 | 293.8 | 423.5
Total ADMD | 180 | 180 | 293.8 | 423.5 | 293.8 | 423.5 | Storage
Average kW ADMD Per House Hold | 1.8 | 1.8 | 7.345 | 10.5875 | 7.345 | 10.5875 |  | 100 | 50 | 25 | 20 | 15 | 10 | 5 | 1
[7 empty] | House only | 1.8 | 1.93 | 2.07 | 2.2 | 2.8 | 3.8 | 5.3 | 7.11
[7 empty] | With 3.68kW EVSE (No smart Charging (SC)) | 3.732 | 3.8 | 3.94 | 4.29 | 4.63 | 5.99 | 8.05 | 10.79
Grand Totals | [6 empty] | With 7.36kW (or two 3.68) EVSE (No smart charging) | 5.3351 | 5.44 | 5.64 | 6.081 | 6.52 | 8.289 | 10.938 | 14.47
[7 empty] | With 7.36kW (or two 3.68) EVSE (With smart charging) | 3.55 | 3.68 | 3.82 | 4.35 | 4.88 | 7.02 | 10.21 | 14.47
[7 empty] | With 5kW (Elec) Storage Heating | 2.9 | 3 | 3.13 | 3.33 | 3.56 | 4.3 | 5.5 | 7.11
Total Diversity Level | 100 | [5 empty] | With 5kW (Elec) Storage Heating + 7.36kW EVSE (No SC) | 5.3351 | 5.44 | 5.64 | 6.081 | 6.52 | 8.289 | 10.938 | 14.47
Total Standard Undiversified | 767.6
Total Standard Diversified | 383.8 | [5 empty] | With 5kW (Elec) Storage Heating + 7.36kW EVSE (With SC) | 3.55 | 3.68 | 3.82 | 4.35 | 4.88 | 7.02 | 10.21 | 14.47
Total CL Undiversified | 1027 | [5 empty] | With 8kW (Elec) Storage Heating | 4.7 | 4.8 | 5.05 | 5.19 | 5.34 | 5.93 | 6.81 | 8
Total CL Diversified | 513.5 | [5 empty] | With 8kW (Elec) Storage Heating + 7.36kW EVSE (No SC) | 5.3351 | 5.44 | 5.64 | 6.081 | 6.52 | 8.289 | 10.938 | 14.47
[7 empty] | With 8kW (Elec) Storage Heating + 7.36kW EVSE (With SC) | 3.55 | 3.68 | 3.82 | 4.35 | 4.88 | 7.02 | 10.21 | 14.47
[7 empty] | With 16kW (Elec) Storage Heating | 9.23 | 9.6 | 10.15 | 10.44 | 10.6 | 11.9 | 13.66 | 16
[7 empty] | With 16kW (Elec) Storage Heating + 7.36kW EVSE (No SC) | 9.23 | 9.6 | 10.15 | 10.44 | 10.6 | 11.9 | 13.66 | 16
[7 empty] | With 16kW (Elec) Storage Heating + 7.36kW EVSE (With SC) | 9.23 | 9.6 | 10.15 | 10.44 | 10.6 | 11.9 | 13.66 | 16
ADMD
Detailed Breakdown
ADMD Calculator for 20+ Properties

## Assumptions
Assumptions | Undiversified Load Levels (kW electrical) | Standard | Cold Load
EVs | EVs
Domestic EV Charge points are 7.36 kW as standard | Non Smart Charge Value | 7.36 | 7.36
"Smart charging" here means a control function that reduces EV charging demand during peak hours | Smart Charge Value | 3.68 | 3.68
Air Source Heat Pumps (ASHP) | Air Source Heat Pumps
5kW equates to 1-2 bedroom house, 8kW to 3-4 bedroom house, 16kW to 5+ bedroom house | 5kW ASHP | 2.41 | 3.38
All values in point above assume insulation is to 1990s standard or better | 8kW ASHP | 4.68 | 6.55
ASHPs here provide both water and space heating and incorporates a Direct Electric Heating Element (backup heater) | 16kW ASHP | 9.37 | 13.12
Ground Source Heat Pumps | Ground Source Heat Pumps
5kW equates to 1-2 bedroom house, 8kW to 3-4 bedroom house, 16kW to 5+ bedroom house | 5kW GSHP | 2.6 | 2.6
All values in point above assume insulation is to 1990s standard or better | 8kW GSHP | 3.8 | 3.8
ASHPs here provide both water and space heating but DO NOT have backup heater | 16kW GSHP | 6.5 | 6.5
Hybrid Heat Pumps | Hybrid Heat Pumps
5kW equates to 1-2 bedroom house, 8kW to 3-4 bedroom house, 16kW to 5+ bedroom house | 5kW Hybrid | 1.22 | 1.22
All values in point above assume insulation is to 1990s standard or better | 8kW Hybrid | 2.69 | 2.69
The Hybrid system here provides both water and space heating but DOES NOT have backup heater | 16kW Hybrid | 4.57 | 4.57
Hybrid means bi-valent or switches to gas when outside temp drops below certain value. 8C threshold here. | Storage Heating
Storage Heating | 5kW Storage | 5 | 5
5kW equates to 1-2 bedroom house, 8kW to 3-4 bedroom house, 16kW to 5+ bedroom house | 8kW Storage | 8 | 8
All values in point above assume insulation is to 1990s standard or better | 16kW Storage | 16 | 16
The storage heating system provides only space heating
Standalone standard household value is around 2kW ADMD
Battery Storage
If sufficiently battery capacity is avaiable at the property or on the feeder the system can recuce ADMD by 40% of peak
Sufficient Battery Capacity means Battery Size in kWH must be at least 3 times that of ADMD without Battery
For example if ADMD of property without battery was 3kW the battery would need at least 9kWh of capacity
The approximation of diversity profile for ADMD vs number of customers can be seen in the graph below

## User Guide
SPEN ADMD Calculator User Guide:
This calculator is designed to determine the level of capacity (in kW) LV mains feeders and substations will need, for both new and existing developments, through understanding of the effects LCTs have on ADMD and the subsequent strain on the network caused.
Simply fill in column D cells 4-13 with the configuration you require prompted by the questions in Column B. The outputs from your "run" can be viewed in Cells D17-20
A standard example is already populated when the user opens an unedited version (V1.06)
All other cells that are locked should not need edited by the user
Drop down menus in some cells are there to assist/reduce error. Otherwise type your number
The options/ ranges for your answers can be seen in column C
A more detailed breakdown of your "run" can be viewed from row 29 onwards
Assumptions and more detailed numbers can be viewed in the "Assumptions" sheet
Each "run" is for one feeder. To calculate total demand on a Substation with for example 3 feeders; Simply sum the results from the 3 individual feeder "runs"
Standard Definition:
Networks need to be designed for the realistic worst case ADMD. Therefore "standard" here means the peak ADMD which occurs during a 1/20 winter in the UK.
Cold Load Pickup Definition:
"Cold Load" is the peak ADMD which occurs during a 1/20 winter in the UK coupled with a significant power cut at this time.
When the fault is remedied and the heat pump systems come back online there is consequently no diversity as everyone on the feeder is attempting to warm their houses at an increased rate at the same time. This puts an additional load above the "standard" design which needs to be catered for if no mitigating technologies are available. Although an extremely unlikely occurrence the knock on effects are severe for the network if not considered.

## Graphs (hidden)
Plugged in AND Charging
<-

## ASHP (hidden)
House Type | m2 | Heat Pump (Heat kW output) Required 2010 insulation | Heat Pump (Heat kW output) Required 1990 insulation | % Delta | Elec kW Draw Continous Worst Case | Elec kW Draw Power Cut Worst Case | Elec kW Draw Power Cut Average Case (No Batt)
1 Bed Flat | 46 | 2.47 | 3.18 | 22.33% | 1.7525 | 2.8125 | 2.4535
2 Bed Flat | 68 | 3.74 | 4.38 | 14.61% | 2.4139 | 3.8739 | 3.3794
Bungalow | 100 | 6.19 | 7.21 | 14.15% | 3.9735 | 6.3768 | 5.5629
Terraced | 106 | 6 | 6.78 | 11.5% | 3.7365 | 5.9965 | 5.2311
Semi Detached | 150 | 7.52 | 8.49 | 11.43% | 4.6789 | 7.5089 | 6.5505
Large Detached | 310 | 15 | 17 | 11.76% | 9.3689 | 15.0356 | 13.1164
|  |  |  | Ratio of "Rated" | 55.11% | 88.44% | 77.16%
|  |  |  | Div Fact | Standard (~0.5) | 0% | None (1)
[9 empty] | 9 Terraced Houses Example 3HS 3MS 3LS |  |  |  | Analysis
[9 empty] | Event | Time | P best Case | P Worst Case | Average | % above normal
[10 empty] | -10 | 0 | 0 | 0 | 0
[9 empty] | Power On | 0 | 33.66 | 33.66 | 33.66 | 0%
[10 empty] | 10 | 33.66 | 33.66 | 33.66 | 0%
[8 empty] | 10 | High Set | 20 | 40.44 | 40.44 | 40.44 | 20.14%
[10 empty] | 30 | 33.66 | 40.44 | 37.05 | 10.07%
[8 empty] | 10 | Medium Set | 40 | 40.44 | 47.22 | 43.83 | 30.21%
[10 empty] | 50 | 33.66 | 47.22 | 40.44 | 20.14%
[8 empty] | 10 | Low Set | 60 | 40.44 | 54 | 47.22 | 40.29%
[9 empty] | Cust | ADMD
[9 empty] | 1 | 2.844
[9 empty] | 25 | 1.58
[9 empty] | 50 | 1.389
[9 empty] | 75 | 1.3
[9 empty] | 100 | 1.276
Power Cut
Power Restored + Compressors Begin
High Set Backups Begin
Medium Set Backups Begin
Low Set Backups Begin
If Heat Pump KW Heat Output > 10kW Backup = 6kW
If Heat Pump KW Heat Output < 10kW Backup = 3kW
Single phase Fault Effect = 62.33% (+7.33% no Diveristy)
Three Phase Fault Effect = 77% (+22% no Diveristy)
Power Cut Duration = 3 Hours in Dead of Winter
Further Effects = House Cold or Batt Discharged
Note on H10: Haynes, Jack: 4.96/9 (worst case rating / Rated Power of Unit)
Note on I10: Haynes, Jack: [Worst Case + Backup (3kW unit)] /Rated power of Unit
Note on J10: Haynes, Jack: Backup Setting Diversity (40% above Normal Worst Case)

## G&WSHP (hidden)
House Type | m2 | Heat Pump (Heat kW output) Required 2010 insulation | Heat Pump (Heat kW output) Required 1990 insulation | GSHP Size Needed (kW) | % Delta | Elec kW Draw Continous Worst Case | Elec kW Draw Power Cut Average Case (No Batt) | ASHP C | Norm GSHP vs ASHP % | ASHP PC | PC GSHP vs ASHP %
1 Bed Flat | 46 | 2.47 | 3.18 |  | 22.33% | Typical Power @ B0/W55 | #VALUE!
2 Bed Flat | 68 | 3.74 | 4.38 |  | 14.61% | 2.6031 | 3.6443
Bungalow | 100 | 6.19 | 7.21 | 9 | 14.15% | 3.8 | 3.8
Terraced | 106 | 6 | 6.78 | 7 | 11.5% | 2.6 | 2.6 | 3.97 | 65.49% | 5.56 | 46.76%
Semi Detached | 150 | 7.52 | 8.49 | 9 | 11.43% | 3.8 | 3.8 | 4.68 | 81.2% | 6.55 | 58.02%
Large Detached | 310 | 15 | 17 | 17 | 11.76% | 6.5 | 6.5 | 9.37 | 69.37% | 13.12 | 49.54%
[5 empty] | Ratio to "Rated" | 42% | 42% |  | 72.02% |  | 51.44%
[5 empty] | Div Fact | Standard (~0.5) | None (1)
[5 empty] | Ratio of 35/55 |  | 26*C Bandwith
1.2861
[5 empty] | Size | Typical Current @ B0/W35 | Typical Power @ B0/W55
[5 empty] | 7 | 8.8 | 2.6031
[5 empty] | 9 | 12.7 | 3.7567
[5 empty] | 17 | 22 | 6.5077
Note on J10: Haynes, Jack: Backup Setting Diversity (40% above Normal Worst Case)

## HybridHP (hidden)
House Type | m2 | Heat Pump (Heat kW output) Required 2010 insulation | Heat Pump (Heat kW output) Required 1990 insulation | GSHP Size Needed (kW) | % Delta | Elec kW Draw Continous Worst Case | Elec kW Draw Power Cut Average Case (No Batt) | ASHP C | Norm GSHP vs HyHP % | ASHP PC | PC HyHP vs ASHP %
1 Bed Flat | 46 | 2.47 | 3.18 |  | 22.33% | 0 | 0
2 Bed Flat | 68 | 3.74 | 4.38 |  | 14.61% | Current Drawn (A) | #VALUE!
Bungalow | 100 | 6.19 | 7.21 | 9 | 14.15% | 3.8 | 3.8
Semi Detached | 150 | 5 | 5 | 5 | 0% | 1.22 | 1.22 | 2.41 | 50.62% | 6.55 | 18.63%
Large Detached | 310 | 8 | 8 | 8 | 0% | 2.69 | 2.69 | 4.68 | 57.48% | 13.12 | 20.5%
[5 empty] | Ratio to "Rated" | 29% | 29% |  | 54.05% |  | 19.56%
[5 empty] | Div Fact | Standard (~0.5) | None (1)
Altherma Hybrid System - ASHP section - Capacity, CoP and Running Current | [7 empty] | Typical House Heat Loss % of total at -5oC
Ambient Air Temperature | Heating Water Flow Temp. (oC) | 5 kW System |  |  | 8 kW System
|  | Heat Out (kW) | CoP | Current Drawn (A) | Heat Out (kW) | CoP | Current Drawn (A) |  | Actual Price per kWh with gas | Actual price per kWh with electricity (5kW) | Actual price per kWh with electricity (8kW)
20oC | 30 | 6.02 | 814% | 3.22 | 13.81 | 614% | 9.78 |  | 0 | 1.5971 | 2.1173
19oC | 31 | 5.87 | 772% | 3.3 | 13.39 | 585% | 9.96 |  | 0 | 1.6839 | 2.2222
18 | 32 | 5.73 | 744% | 3.35 | 12.96 | 559% | 10.09 |  | 0 | 1.7473 | 2.3256
17 | 33 | 5.58 | 715% | 3.39 | 12.55 | 532% | 10.26 |  | 0 | 1.8182 | 2.4436
16 | 34 | 5.44 | 680% | 3.48 | 12.13 | 505% | 10.43 |  | 0 | 1.9118 | 2.5743
15 | 35 | 5.29 | 653% | 3.52 | 11.72 | 480% | 10.61 |  | 0 | 1.9908 | 2.7083
14 | 36 | 5.24 | 602% | 3.78 | 11.33 | 453% | 10.87 |  | 0 | 2.1595 | 2.8698
13 | 37 | 5.18 | 551% | 4.09 | 10.96 | 428% | 11.13 |  | 0 | 2.3593 | 3.0374
12 | 38 | 5.12 | 517% | 4.3 | 10.59 | 404% | 11.39 |  | 0 | 2.5145 | 3.2178
11 | 39 | 5.08 | 475% | 4.65 | 10.4 | 390% | 11.61 |  | 0 | 2.7368 | 3.3333
10 | 40 | 5.03 | 445% | 4.91 | 10.21 | 375% | 11.83 | 48% | 0 | 2.9213 | 3.4667
9 | 41 | 5 | 410% | 5.3 | 10.01 | 363% | 12 | 52% | 0 | 3.1707 | 3.5813
8 | 42 | 4.97 | 382% | 5.65 | 9.82 | 348% | 12.26 | 56% | 0 | 3.4031 | 3.7356
7 | 43 | 4.95 | 356% | 6.04 | 9.64 | 336% | 12.48 | 59% | 0 | 3.6517 | 3.869
6 | 44 | 4.92 | 335% | 6.39 | 9.3 | 318% | 12.7 | 62% | 0 | 3.8806 | 4.0881
5 | 45 | 4.89 | 313% | 6.78 | 8.97 | 303% | 12.87 | 66% | 0 | 4.1534 | 4.2904
4 | 46 | 4.84 | 292% | 7.22 | 8.61 | 289% | 12.96 | 69% | 0 | 4.4521 | 4.4983
3 | 47 | 4.78 | 270% | 7.7 | 8.29 | 275% | 13.09 | 72% | 0 | 4.8148 | 4.7273
2 | 48 | 4.73 | 253% | 8.13 | 7.98 | 265% | 13.09 | 76% | 0 | 5.1383 | 4.9057
1 | 49 | 4.67 | 236% | 8.61 | 7.78 | 253% | 13.39 | 80% | 0 | 5.5085 | 5.1383
0 | 50 | 4.62 | 222% | 9.04 | 7.54 | 242% | 13.52 | 83% | 0 | 5.8559 | 5.3719
-1 | 51 | 4.53 | 211% | 9.35 | 7.23 | 230% | 13.65 | 87% | 0 | 6.1611 | 5.6522
-2 | 52 | 4.44 | 201% | 9.61 | 6.94 | 218% | 13.83 | 90% | 0 | 6.4677 | 5.9633
-3 | 53 | 4.34 | 190% | 9.91 | 6.69 | 208% | 13.96 | 93% | 0 | 6.8421 | 6.25
-4 | 54 | 4.25 | 182% | 10.17 | 6.45 | 199% | 14.09 | 96% | 0 | 7.1429 | 6.5327
-5 | 55 | 4.16 | 173% | 10.48 | 6.21 | 190% | 14.22 | 100% | 0 | 7.5145 | 6.8421
Crossover point where electricity is cheaper per kWh for a 5kW system
Crossover point where electricity is cheaper per kWh for a 8kW system
|  | Price of electricity per kWh (in pence) |  |  |  | 13
|  | Price of gas per kWh (in pence) |  |  |  | 3
Note on J9: Haynes, Jack: Backup Setting Diversity (40% above Normal Worst Case)

## Data (hidden)
1
25
50
100
Yes
No
0 | 0
5 | 7.36
8
16

## HP Variables Calc New (hidden)
Equation Factors
Finding Value of Best Fit | X^ Value | Gradient |  |  | EV | HP | BS | PV | S
House only | 0.165 | 3.862 |  |  | 0.9 | 0.7 | 0.08 | 0.5 | 1.93
With 3.68kW EVSE | 0.15 | 7
With 7.36kW (or two 3.68) EVSE | 0.15 | 10 |  |  | Equipment Ratings
With 3.68kW HP (10kW Heat Output) | 0.236 | 6.723 |  |  | HP + BS + PV |  | EVSE
With 3.68kW HP + 7.36kW EVSE | 0.194 | 12.867 |  |  | 3.68 |  | 7.36
With 3.68kWH Battery storage | 0.164 | 1.67
With 3.68kW EVSE + 3.68kWH Battery storage | 0.078 | 4.92 |  |  | Overall Error
With 7.36kW EVSE + 3.68kWH Battery storage | 0.078 | 7.04 |  |  | 24.61% | Whole
With 3.68kW HP + 3.68kWH Battery storage | 0.164 | 4.73 |  |  | 24.48% | >25
With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage | 0.123 | 9.05
With 3.68kWH Battery storage +3kW PV | 0.167 | 1.23
With 3.68kW EVSE + 3.68kWH Battery storage + 3kW PV | 0.081 | 3.633
With 7.36kW EVSE + 3.68kWH Battery storage + 3kW PV | 0.081 | 5.194
With 3.68kW HP + 3.68kWH Battery storage + 3kW PV | 0.167 | 3.491
With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage +3kW PV | 0.125 | 6.678
Mean | 0.14153 | 5.8725
| Real | [6 empty] | Calculated (Old 10kW HP) |  |  |  |  | Error
Increases a customers (No Battery or PV) | 100 | 75 | 50 | 25 | 1 |  |  | 100 | 75 | 50 | 25 | 1 | 100 | 75 | 50 | 25 | 1
House only | 2.066 | 1.993 | 1.929 | 1.799 | 4.113 |  |  | 1.93 | 1.93 | 1.93 | 1.93 | 1.93 | 6.583% | 3.161% | 0.05184% | 7.282% | 53.08%
With 3.68kW EVSE | 3.732 | 3.757 | 3.802 | 3.943 | 7.21 |  |  | 2.7317 | 2.8452 | 3.0133 | 3.3239 | 5.242 | 26.8% | 24.27% | 20.75% | 15.7% | 27.3%
With 7.36kW (or two 3.68) EVSE | 5.3351 | 5.3708 | 5.4351 | 5.6367 | 10.307 |  |  | 4.4576 | 4.6429 | 4.9171 | 5.4239 | 8.554 | 16.45% | 13.55% | 9.531% | 3.774% | 17.01%
With 3.68kW HP (10kW Heat Output) | 2.3364 | 2.4166 | 2.6043 | 3.14 | 6.759 |  |  | 2.3481 | 2.4457 | 2.5902 | 2.8572 | 4.506 | 0.5026% | 1.204% | 0.5406% | 9.007% | 33.33%
With 3.68kW HP + 7.36kW EVSE | 5.4989 | 5.6118 | 5.8632 | 6.575 | 13.088 |  |  | 5.8 | 6.041 | 6.3979 | 7.0573 | 11.13 | 5.475% | 7.649% | 9.118% | 7.335% | 14.96%
With 3.68kWH Battery storage | 1.2396 | 1.1958 | 1.1574 | 1.0794 | 2.4678 |  |  | 0.85234 | 0.88776 | 0.94019 | 1.0371 | 1.6356 | 31.24% | 25.76% | 18.77% | 3.919% | 33.72%
With 3.68kW EVSE + 3.68kWH Battery storage | 2.2392 | 2.2542 | 2.2812 | 2.3658 | 4.326 |  |  | 2.5783 | 2.6854 | 2.844 | 3.1372 | 4.9476 | 15.14% | 19.13% | 24.67% | 32.61% | 14.37%
With 7.36kW EVSE + 3.68kWH Battery storage | 3.201 | 3.2225 | 3.2611 | 3.382 | 6.1842 |  |  | 4.3042 | 4.4831 | 4.7479 | 5.2373 | 8.2596 | 34.46% | 39.12% | 45.59% | 54.86% | 33.56%
With 3.68kW HP + 3.68kWH Battery storage | 1.4018 | 1.45 | 1.5626 | 1.884 | 4.0554 |  |  | 2.1947 | 2.2859 | 2.421 | 2.6705 | 4.2116 | 56.56% | 57.65% | 54.94% | 41.75% | 3.851%
With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage | 3.2994 | 3.3671 | 3.5179 | 3.945 | 7.8528 |  |  | 5.6466 | 5.8812 | 6.2286 | 6.8707 | 10.8356 | 71.14% | 74.67% | 77.05% | 74.16% | 37.98%
With 3.68kWH Battery storage +3kW PV | 1.2024 | 1.1599 | 1.1227 | 1.047 | 2.3938 |  |  | -0.10652 | -0.11094 | -0.1175 | -0.12961 | -0.2044 | 0% | 0% | 0% | 0% | 0%
With 3.68kW EVSE + 3.68kWH Battery storage + 3kW PV | 2.172 | 2.1866 | 2.2128 | 2.2948 | 4.1962 |  |  | 1.6194 | 1.6867 | 1.7863 | 1.9705 | 3.1076 | 25.44% | 22.86% | 19.27% | 14.13% | 25.94%
With 7.36kW EVSE + 3.68kWH Battery storage + 3kW PV | 3.105 | 3.1258 | 3.1632 | 3.2806 | 5.9987 |  |  | 3.3453 | 3.4844 | 3.6902 | 4.0705 | 6.4196 | 7.741% | 11.47% | 16.66% | 24.08% | 7.017%
With 3.68kW HP + 3.68kWH Battery storage + 3kW PV | 1.3598 | 1.4065 | 1.5157 | 1.8275 | 3.9338 |  |  | 1.8492 | 1.8386 | 1.8237 | 1.7986 | 1.6863 | 35.99% | 30.72% | 20.32% | 1.581% | 57.13%
With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage +3kW PV | 3.2004 | 3.2661 | 3.4124 | 3.8267 | 7.6172 |  |  | 4.6877 | 4.8825 | 5.1709 | 5.7039 | 8.9956 | 46.47% | 49.49% | 51.53% | 49.06% | 18.1%
|  |  | PV Additional Factor |  | 0.97
| Calculated *5kW Normal |  |  |  |  | *5kW Power Cut
| 100 | 75 | 50 | 25 | 1 | 100 | 75 | 50 | 25 | 1
House only | 2.066 | 1.993 | 1.929 | 1.799 | 4.113
With 3.68kW HP (10kW Heat Output) | 2.3364 | 2.4166 | 2.6043 | 3.14 | 6.759
With 3.68kW HP + 7.36kW EVSE | 5.8 | 6.041 | 6.3979 | 7.0573 | 11.13
With 3.68kW HP + 3.68kWH Battery storage | 2.1947 | 2.2859 | 2.421 | 2.6705 | 4.2116
With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage | 5.6466 | 5.8812 | 6.2286 | 6.8707 | 10.8356
With 3.68kW HP + 3.68kWH Battery storage + 3kW PV | 1.8492 | 1.8386 | 1.8237 | 1.7986 | 1.6863
With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage +3kW PV | 4.6877 | 4.8825 | 5.1709 | 5.7039 | 8.9956
| Calculated *8kW Normal |  |  |  |  | *8kW Power Cut
| 100 | 75 | 50 | 25 | 1 | 100 | 75 | 50 | 25 | 1
House only | 1.6867 | 1.93 | 1.93 | 1.93 | 1.93 | 0.25442 | 1.93 | 1.93 | 1.93 | 1.93
With 3.68kW HP (10kW Heat Output) | 2.3481 | 2.4457 | 2.5902 | 2.8572 | 4.506 | 2.3481 | 2.4457 | 2.5902 | 2.8572 | 4.506
With 3.68kW HP + 7.36kW EVSE | 5.8 | 6.041 | 6.3979 | 7.0573 | 11.13 | 5.8 | 6.041 | 6.3979 | 7.0573 | 11.13
With 3.68kW HP + 3.68kWH Battery storage | 2.1947 | 2.2859 | 2.421 | 2.6705 | 4.2116 | 2.1947 | 2.2859 | 2.421 | 2.6705 | 4.2116
With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage | 5.6466 | 5.8812 | 6.2286 | 6.8707 | 10.8356 | 5.6466 | 5.8812 | 6.2286 | 6.8707 | 10.8356
With 3.68kW HP + 3.68kWH Battery storage + 3kW PV | 1.8492 | 1.8386 | 1.8237 | 1.7986 | 1.6863 | 1.8492 | 1.8386 | 1.8237 | 1.7986 | 1.6863
With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage +3kW PV | 4.6877 | 4.8825 | 5.1709 | 5.7039 | 8.9956 | 4.6877 | 4.8825 | 5.1709 | 5.7039 | 8.9956
| Calculated *16kW Normal |  |  |  |  | *16kW Power Cut
| 100 | 75 | 50 | 25 | 1 | 100 | 75 | 50 | 25 | 1
House only | 0 | 1.93 | 1.93 | 1.93 | 1.93 | 0 | 1.93 | 1.93 | 1.93 | 1.93
With 3.68kW HP (10kW Heat Output) | 2.3481 | 2.4457 | 2.5902 | 2.8572 | 4.506 | 2.3481 | 2.4457 | 2.5902 | 2.8572 | 4.506
With 3.68kW HP + 7.36kW EVSE | 5.8 | 6.041 | 6.3979 | 7.0573 | 11.13 | 5.8 | 6.041 | 6.3979 | 7.0573 | 11.13
With 3.68kW HP + 3.68kWH Battery storage | 2.1947 | 2.2859 | 2.421 | 2.6705 | 4.2116 | 2.1947 | 2.2859 | 2.421 | 2.6705 | 4.2116
With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage | 5.6466 | 5.8812 | 6.2286 | 6.8707 | 10.8356 | 5.6466 | 5.8812 | 6.2286 | 6.8707 | 10.8356
With 3.68kW HP + 3.68kWH Battery storage + 3kW PV | 1.8492 | 1.8386 | 1.8237 | 1.7986 | 1.6863 | 1.8492 | 1.8386 | 1.8237 | 1.7986 | 1.6863
With 3.68kW HP + 7.36kW EVSE + 3.68kWH Battery storage +3kW PV | 4.6877 | 4.8825 | 5.1709 | 5.7039 | 8.9956 | 4.6877 | 4.8825 | 5.1709 | 5.7039 | 8.9956